## Slide 1: Thermal Simulation Discussion
09/06/2017
Yueming Li, Thermal Engineer, Facebook
John Fernandes, Thermal Engineer, Facebook
Joshua Held, Mechanical Engineer, Facebook
Jia Ning, Hardware Engineer, Facebook

## Slide 2: Comparison of Major Options
 | Option 7 | Option 13 | Option 14
Small Form Factor Size | 78x110 | 78x110 | 74x110
Pressure Drop (@150LFM) | 8.81 Pa | 8.38 Pa | 8.56 Pa
ASIC HS Size | 45mm (L) x 59.8mm (W) | 45mm (L) x 63.3 mm (W) | 45mm (L) x 66mm (W)
ASIC HS Fin Height | 7.56mm | 7.2mm | 7.2mm
ASIC Tcase | 107.8°C | 97.5°C | 93.1°C
QSFP Tcase | 69.7°C | 71.9°C | 70.4°C
Conditions for simulation results above in the chart: 150 LFM, cold-aisle cases, ASIC power 25W

## Slide 3: Benefits of New Options (13, 14)
Flipping the ASIC to top side -> Flexible HS height
Getting rid of side connectors -> Wider ASIC heat sink
Lower ASIC Tcase
Case # | Input parameters |  |  | Output parameters |  |  |  |  |  |  |  |  |  |  |  |  |  | 
 | I/O | ASIC 1 Power (W) | Airflow Direction or I/O Location | ASIC Tcase_max (°C) |  |  |  |  |  |  | I/O Module Tcase_max (°C) |  |  |  |  |  |  | 
 |  |  |  | 105°C |  |  |  |  |  |  | 70°C |  |  |  |  |  |  | 
 |  |  |  | 150 | 200 | 250 | 300 | 400 | 500 | 750 | 150 | 200 | 250 | 300 | 400 | 500 | 750 | LFM
14-A1 - with HS | 2x QSFP | 15 | Cold-aisle | 73.2 | 67.1 | 63.3 | 60.7 | 57.3 | 55.0 |  | 68.9 | 63.9 | 60.7 | 58.6 | 55.8 | 54.0 |  | 
14-A2 - with HS | 2x QSFP | 20 | Cold-aisle | 83.1 | 75.7 | 71.0 | 67.8 | 63.6 | 60.8 |  | 69.7 | 64.3 | 61.1 | 58.8 | 55.9 | 54.2 |  | 
14-A3 - with HS | 2x QSFP | 25 | Cold-aisle | 93.1 | 84.2 | 78.7 | 74.9 | 69.8 | 66.5 |  | 70.4 | 64.8 | 61.5 | 59.0 | 56.1 | 54.3 |  | 
14-A4 - with HS | 2x QSFP | 30 | Cold-aisle | 103.0 | 92.8 | 86.4 | 82.0 | 76.1 | 72.3 |  | 71.1 | 65.3 | 61.8 | 59.3 | 56.2 | 54.4 |  | 
14-A5 - with HS | 2x QSFP | 35 | Cold-aisle | 113.0 | 101.3 | 94.1 | 89.1 | 82.4 | 78.0 |  | 71.9 | 65.7 | 62.1 | 59.5 | 56.4 | 54.5 |  | 
#7
#14
Case # | Input parameters |  |  | Output parameters |  |  |  |  |  |  |  |  |  |  |  |  |  | 
 | I/O | ASIC 1 Power (W) | Airflow Direction or I/O Location | ASIC Tcase_max (°C) |  |  |  |  |  |  | I/O Module Tcase_max (°C) |  |  |  |  |  |  | 
 |  |  |  | 105°C |  |  |  |  |  |  | 70°C |  |  |  |  |  |  | 
 |  |  |  | 150 | 200 | 250 | 300 | 400 | 500 | 750 | 150 | 200 | 250 | 300 | 400 | 500 | 750 | LFM
7-A1 - with HS | 2x QSFP-Bottom | 15 | Cold-aisle | 82.2 | 75.4 | 71.1 | 67.9 | 63.7 | 60.8 |  | 68.5 | 64.1 | 61.3 | 59.2 | 56.6 | 54.8 |  | 
7-A2 - with HS | 2x QSFP-Bottom | 20 | Cold-aisle | 95.0 | 86.6 | 81.1 | 77.2 | 71.8 | 68.3 |  | 69.1 | 64.5 | 61.5 | 59.5 | 56.7 | 54.9 |  | 
7-A3 - with HS | 2x QSFP-Bottom | 25 | Cold-aisle | 107.8 | 97.7 | 91.1 | 86.4 | 80.0 | 75.8 |  | 69.7 | 64.9 | 61.8 | 59.7 | 56.8 | 55.0 |  | 
7-A4 - with HS | 2x QSFP-Bottom | 30 | Cold-aisle | 120.6 | 108.8 | 101.2 | 95.7 | 88.2 | 83.2 |  | 70.3 | 65.3 | 62.1 | 59.9 | 57.0 | 55.1 |  | 
7-A5 - with HS | 2x QSFP-Bottom | 35 | Cold-aisle | 133.5 | 120.0 | 111.2 | 104.9 | 96.4 | 90.7 |  | 70.9 | 65.7 | 62.4 | 60.1 | 57.1 | 55.2 |  | 

## Slide 4: Comparison between 13 and 14
Case # |  | Input parameters |  | Output parameters |  |  |  |  |  |  |  |  |  |  |  |  |  | 
 | I/O | ASIC 1 Power (W) | Airflow Direction or I/O Location | ASIC Tcase_max (°C) |  |  |  |  |  |  | I/O Module Tcase_max (°C) |  |  |  |  |  |  | 
 |  |  |  | 105°C |  |  |  |  |  |  | 70°C |  |  |  |  |  |  | 
 |  |  |  | 150 | 200 | 250 | 300 | 400 | 500 | 750 | 150 | 200 | 250 | 300 | 400 | 500 | 750 | LFM
14-A1 - with HS | 2x QSFP | 15 | Cold-aisle | 73.2 | 67.1 | 63.3 | 60.7 | 57.3 | 55.0 |  | 68.9 | 63.9 | 60.7 | 58.6 | 55.8 | 54.0 |  | 
14-A2 - with HS | 2x QSFP | 20 | Cold-aisle | 83.1 | 75.7 | 71.0 | 67.8 | 63.6 | 60.8 |  | 69.7 | 64.3 | 61.1 | 58.8 | 55.9 | 54.2 |  | 
14-A3 - with HS | 2x QSFP | 25 | Cold-aisle | 93.1 | 84.2 | 78.7 | 74.9 | 69.8 | 66.5 |  | 70.4 | 64.8 | 61.5 | 59.0 | 56.1 | 54.3 |  | 
14-A4 - with HS | 2x QSFP | 30 | Cold-aisle | 103.0 | 92.8 | 86.4 | 82.0 | 76.1 | 72.3 |  | 71.1 | 65.3 | 61.8 | 59.3 | 56.2 | 54.4 |  | 
14-A5 - with HS | 2x QSFP | 35 | Cold-aisle | 113.0 | 101.3 | 94.1 | 89.1 | 82.4 | 78.0 |  | 71.9 | 65.7 | 62.1 | 59.5 | 56.4 | 54.5 |  | 
#13
#14
Case # |  | Input parameters |  | Output parameters |  |  |  |  |  |  |  |  |  |  |  |  |  | 
 | I/O | ASIC 1 Power (W) | Airflow Direction or I/O Location | ASIC Tcase_max (°C) |  |  |  |  |  |  | I/O Module Tcase_max (°C) |  |  |  |  |  |  | 
 |  |  |  | 105°C |  |  |  |  |  |  | 70°C |  |  |  |  |  |  | 
 |  |  |  | 150 | 200 | 250 | 300 | 400 | 500 | 750 | 150 | 200 | 250 | 300 | 400 | 500 | 750 | LFM
13-A1 - with HS | 2x QSFP-Bottom | 15 | Cold-aisle | 76.1 | 69.3 | 65.1 | 62.2 | 58.3 | 55.8 |  | 69.9 | 64.5 | 61.1 | 58.8 | 55.9 | 54.1 |  | 
13-A2 - with HS | 2x QSFP-Bottom | 20 | Cold-aisle | 86.8 | 78.4 | 73.2 | 69.6 | 64.9 | 61.8 |  | 70.9 | 65.2 | 61.6 | 59.2 | 56.1 | 54.3 |  | 
13-A3 - with HS | 2x QSFP-Bottom | 25 | Cold-aisle | 97.5 | 87.5 | 81.3 | 77.1 | 71.4 | 67.8 |  | 71.9 | 65.8 | 62.0 | 59.5 | 56.3 | 54.4 |  | 
13-A4 - with HS | 2x QSFP-Bottom | 30 | Cold-aisle | 108.2 | 96.6 | 89.5 | 84.5 | 78.0 | 73.7 |  | 72.9 | 66.4 | 62.5 | 59.8 | 56.6 | 54.6 |  | 
13-A5 - with HS | 2x QSFP-Bottom | 35 | Cold-aisle | 118.8 | 105.7 | 97.6 | 92.0 | 84.5 | 79.7 |  | 73.9 | 67.0 | 62.9 | 60.2 | 56.8 | 54.7 |  | 
ASIC temperature for #14 is slightly better than #13
  Back-side connector of #14 prevents bypass underneath the HS
  #13 has 1 fin less compared to #14 due to side connector placement

## Slide 5: I/O Cooling for Hot-aisle cases – SFP+?
Take Enumeration #14 (hot-aisle cases @ 250LFM; 25W) as an example
 | Dual QSFP+ | Quad SFP+
Power | 2 x 3.5 W | 4 x 1.5 W
Width | 18.65 mm (each QSFP) | 54.77 mm (cage)
Temperature Spec (°C) | 70°C (Commercial) /85°C (Industrial) | 
Simulation Tcase (°C) | 95.5 | 89.7
Approach air temperature | 74.0 | 78.8
Case # |  | Input parameters |  |  |  |  | Output parameters |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
 | I/O | ASIC 1 Power (W) | ASIC 1 Location | PCB Board Size | DRAM Location | Airflow Direction or I/O Location | ASIC Tcase_max (°C) |  |  |  |  |  |  | I/O Module Tcase_max (°C) |  |  |  |  |  |  | I/O Module approach Tair |  |  |  |  |  |  | 
 |  |  |  |  |  |  | 105°C |  |  |  |  |  |  | 70°C / 85°C |  |  |  |  |  |  |  |  |  |  |  |  |  | 
 |  |  |  |  |  |  | 150 | 200 | 250 | 300 | 400 | 500 | 750 | 150 | 200 | 250 | 300 | 400 | 500 | 750 | 150 | 200 | 250 | 300 | 400 | 500 | 750 | LFM
14-A6 - with HS | 2x QSFP | 15 | Top | 14-small | N/A | Hot-aisle | 84.0 | 79.9 | 77.3 | 75.6 | 73.3 | 71.8 | 69.4 | 102.3 | 94.2 | 89.1 | 85.5 | 81.0 | 78.3 | 74.4 | 74.1 | 69.4 | 66.5 | 64.6 | 62.3 | 60.9 | 59.0 | 
14-A7 - with HS | 2x QSFP | 20 | Top | 14-small | N/A | Hot-aisle | 93.4 | 88.0 | 84.7 | 82.4 | 79.4 | 77.4 | 74.2 | 107.6 | 98.2 | 92.3 | 88.2 | 83.1 | 80.0 | 75.5 | 80.2 | 74.0 | 70.3 | 67.8 | 64.7 | 62.8 | 60.3 | 
14-A8 - with HS | 2x QSFP | 25 | Top | 14-small | N/A | Hot-aisle | 102.7 | 96.1 | 92.0 | 89.1 | 85.4 | 82.9 | 79.0 | 113.0 | 102.2 | 95.5 | 90.9 | 85.2 | 81.6 | 76.7 | 86.4 | 78.7 | 74.0 | 70.9 | 67.1 | 64.7 | 61.6 | 
14-A9 - with HS | 2x QSFP | 30 | Top | 14-small | N/A | Hot-aisle | 112.1 | 104.2 | 99.3 | 95.9 | 91.4 | 88.5 | 83.8 | 118.3 | 106.2 | 98.8 | 93.7 | 87.2 | 83.3 | 77.8 | 92.5 | 83.3 | 77.8 | 74.1 | 69.5 | 66.7 | 62.9 | 
14-A10 - with HS | 2x QSFP | 35 | Top | 14-small | N/A | Hot-aisle | 121.5 | 112.3 | 106.6 | 102.7 | 97.5 | 94.0 | 88.6 | 123.7 | 110.3 | 102.0 | 96.4 | 89.3 | 85.0 | 78.9 | 98.6 | 88.0 | 81.6 | 77.2 | 71.9 | 68.6 | 64.2 | 
14-A6 - with HS | 4x SFP | 15 | Top | 14-small | N/A | Hot-aisle | 83.7 | 79.9 | 77.4 | 75.7 | 73.5 | 72.0 | 69.7 | 94.7 | 87.5 | 82.9 | 80.3 | 76.8 | 74.3 | 70.7 | 77.7 | 72.8 | 69.8 | 67.7 | 65.1 | 63.4 | 61.0 | 
14-A7 - with HS | 4x SFP | 20 | Top | 14-small | N/A | Hot-aisle | 93.1 | 88.0 | 84.7 | 82.5 | 79.5 | 77.5 | 74.5 | 100.1 | 91.5 | 86.0 | 82.8 | 78.6 | 75.8 | 71.8 | 84.5 | 78.2 | 74.3 | 71.6 | 68.1 | 66.0 | 62.9 | 
14-A8 - with HS | 4x SFP | 25 | Top | 14-small | N/A | Hot-aisle | 102.4 | 96.0 | 92.1 | 89.3 | 85.6 | 83.1 | 79.4 | 105.5 | 95.5 | 89.7 | 85.6 | 81.0 | 77.7 | 72.9 | 91.3 | 83.5 | 78.8 | 75.5 | 71.3 | 68.6 | 64.7 | 
14-A9 - with HS | 4x SFP | 30 | Top | 14-small | N/A | Hot-aisle | 111.7 | 104.2 | 99.4 | 96.0 | 91.7 | 88.7 | 84.3 | 110.9 | 99.2 | 92.9 | 88.4 | 83.3 | 79.5 | 74.3 | 98.1 | 88.9 | 83.3 | 79.4 | 74.5 | 71.2 | 66.7 | 
14-A10 - with HS | 4x SFP | 35 | Top | 14-small | N/A | Hot-aisle | 121.1 | 112.3 | 106.8 | 102.8 | 97.7 | 94.3 | 89.1 | 116.3 | 103.3 | 96.1 | 91.1 | 85.0 | 81.3 | 75.3 | 104.8 | 94.3 | 87.8 | 83.3 | 77.5 | 73.8 | 68.5 | 
I/O module is still the gating factor for hot-aisle use cases. It seems not solvable by form factor selection since the approaching air temperature is already close/higher than 70°C specification.