runBMC

BMC daughter board I/O specification

V0.11

Authors: 
Eric Shobe, Hardware Engineer, Salesforce
Jared Mednick, Hardware Engineer, Salesforce

# License

Contributions to this Specification are made under the terms and conditions set forth in Open Web Foundation Contributor License Agreement (“OWF CLA 1.0”) (“Contribution License”) by:

Eric Shobe, Salesforce

Jared Mednick, Salesforce

You can review the signed copies of the applicable Contributor License(s) for this Specification on the OCP website at http://www.opencompute.org/products/specsanddesign

Usage of this Specification is governed by the terms and conditions set forth in Open Web Foundation Final Specification Agreement (“OWFa 1.0”)

You can review the applicable Specification License(s) executed by the above referenced contributors to this Specification on the OCP website at http://www.opencompute.org/participate/legal-documents/

Note:  The following clarifications, which distinguish technology licensed in the Contribution License and/or Specification License from those technologies merely referenced (but not licensed),  were accepted by the Incubation Committee of the OCP:

None

NOTWITHSTANDING THE FOREGOING LICENSES, THIS SPECIFICATION IS PROVIDED BY OCP "AS IS" AND OCP EXPRESSLY DISCLAIMS ANY WARRANTIES (EXPRESS, IMPLIED, OR OTHERWISE), INCLUDING IMPLIED WARRANTIES OF MERCHANTABILITY, NON-INFRINGEMENT, FITNESS FOR A PARTICULAR PURPOSE, OR TITLE, RELATED TO THE SPECIFICATION. NOTICE IS HEREBY GIVEN, THAT OTHER RIGHTS NOT GRANTED AS SET FORTH ABOVE, INCLUDING WITHOUT LIMITATION, RIGHTS OF THIRD PARTIES WHO DID NOT EXECUTE THE ABOVE LICENSES, MAY BE IMPLICATED BY THE IMPLEMENTATION OF OR COMPLIANCE WITH THIS SPECIFICATION. OCP IS NOT RESPONSIBLE FOR IDENTIFYING RIGHTS FOR WHICH A LICENSE MAY BE REQUIRED IN ORDER TO IMPLEMENT THIS SPECIFICATION.  THE ENTIRE RISK AS TO IMPLEMENTING OR OTHERWISE USING THE SPECIFICATION IS ASSUMED BY YOU. IN NO EVENT WILL OCP BE LIABLE TO YOU FOR ANY MONETARY DAMAGES WITH RESPECT TO ANY CLAIMS RELATED TO, OR ARISING OUT OF YOUR USE OF THIS SPECIFICATION, INCLUDING BUT NOT LIMITED TO ANY LIABILITY FOR LOST PROFITS OR ANY CONSEQUENTIAL, INCIDENTAL, INDIRECT, SPECIAL OR PUNITIVE DAMAGES OF ANY CHARACTER FROM ANY CAUSES OF ACTION OF ANY KIND WITH RESPECT TO THIS SPECIFICATION, WHETHER BASED ON BREACH OF CONTRACT, TORT (INCLUDING NEGLIGENCE), OR OTHERWISE, AND EVEN IF OCP HAS BEEN ADVISED OF THE POSSIBILITY OF SUCH DAMAGE.

# Table of Contents

1.	License	2

2.	Table of Contents	3

3.	Scope	5

4.	Overview	6

5.	BMC Daughter Board Signaling Interface	6

5.1	Signal Function Groups	6

5.2	Signal Requirements and Descriptions	7

5.2.1	ADC	7

5.2.2	PCIe	7

5.2.3	1GbT Ethernet and RGMII	7

5.2.4	VGA	8

5.2.5	RMII/NC-SI	8

5.2.6	JTAG	8

5.2.7	USB host	8

5.2.8	USB device	9

5.2.9	SPI Master Interface for Firmware	9

5.2.10	SPI Master Interface for Host	9

5.2.11	LCP/eSPI	9

5.2.12	I2C	9

5.2.13	UART	9

5.2.14	PWM	10

5.2.15	TACH	10

5.2.16	PECI	10

5.2.17	GPIO	10

5.2.18	SGPIO	10

5.2.19	SCIPME	10

5.2.20	RESET	11

5.2.21	WATCHDOG	11

5.2.22	INDICATOR	11

5.2.23	Reserved	11

5.3	Pin Definition	11

5.4	Signal Priority and Nomenclature	14

6.	Power	22

6.1	Electrical Requirements	22

7.	Mechanical	23

7.1	Form Factor	23

7.2	Mating Connector	24

8.	Thermal	24

9.	References	24

# Scope

This document defines the technical specifications for the runBMC used in Open Compute Project.

# Overview

This document describes the runBMC daughter board card design for use with Open Compute Project motherboards. This specification defines the interface between the Baseboard Management Controller(BMC) subsystem and OCP hardware platforms, such as network or compute motherboards.

The runBMC daughter board interfaces with hardware platforms through a 260 pin SODIMM DDR4 connector, and is intended for mounting into 260-pin edge connector SODIMM DDR4 sockets placed on such platforms.

Figure 1 shows the BMC daughter board I/O connectivity

SFDC TO UPDATE IMAGE BELOW HERE

# BMC Daughter Board Signaling Interface

## Signal Function Groups

Signal function groups can be summarized in Table 1.

Table 1  BMC Function Group Summary

| Function | number of pins for one | Number of IFs | Number of used pins |
| --- | --- | --- | --- |
| Form Factor - 260 SO-DIMM4 |  |  |  |
| Power 3.3V |  |  | 5 |
| HSTL power 1.8V |  |  | 1 |
| LPC_3.3v_or_eSPI_1v8 |  |  | 1 |
| Power 12 V |  |  | 1 |
| Ground |  |  | 38 |
| ADC | 1 | 8 | 8 |
| GPIO/ADC | 1 | 8 | 8 |
| PCIe | 7 | 1 | 7 |
| RGMII/1GT PHY | 14 | 1 | 14 |
| VGA / GPIOs | 7 | 1 | 7 |
| RMII/NC-SI | 10 | 1 | 10 |
| Master JTAG/GPIO | 6 | 1 | 6 |
| USB host | 4 | 1 | 4 |
| USB device | 3 | 1 | 3 |
| SPI for host | 5 | 1 | 5 |
| SPI for host - quad | 7 | 1 | 7 |
| GPIO/BMC Boot SPI - quad | 7 | 1 | 7 |
| LPC/eSPI | 8 | 1 | 8 |
| I2C / GPIOs | 2 | 12 | 24 |
| GPIOs / I2C | 2 | 4 | 8 |
| UARTs (TxD, RxD, CTS, RTS) | 4 | 2 | 8 |
| CONSOLE (Tx, Rx) | 2 | 1 | 2 |
| PWM | 1 | 8 | 8 |
| Tacho/GPIOs | 1 | 16 | 16 |
| PECI / GPIOs | 2 | 1 | 2 |
| GPIOs | 1 | 39 | 39 |
| GPIO/GPIO Expanders (Serial GPIO) | 4 | 1 | 4 |
| SCIPME#/GPIO | 2 | 1 | 2 |
| Reset and Power Good | 1 | 2 | 2 |
| Watchdogs/GPIO | 1 | 2 | 2 |
| BOOT_IND# / GPIO | 1 | 1 | 1 |
| RESERVED/KLUDGE | 1 | 2 | 2 |

## Signal Requirements and Descriptions

## ADC

The Interface has 16 voltage sensing channels available to use. 8 of these are primary functional features that may be multiplexed as GPIO’s as secondary functions.  The remaining 8 primarily function as GPIO but may be configured as ADC if desired.

## PCIe

The PCIe connection supports a PCI-Express Gen 2 One Lane (x1) connection.

## Ethernet and RGMII

The interface shall allow flexibility for a Ethernet interface as primary function as shown below in “1GbT Interface”.  Secondary functionally I/Os allow for a RGMII interface to be routed over the connector if desired as shown in the “RGMII interface”

Figure 0-1 1GbT Interface

Figure 0-2 RGMII Interface

## VGA

TODO:

## RMII/NC-SI

TODO:

## JTAG

Interface defines a single JTAG, which is meant to act as a master.  The typical 5 signals are defined including RTCK as a sixth signal not typically used in master applications.

JTAG1TRST : Defines Test Rest, output from BMC

JTAG1TMS : Test Mode Select, output from BMC

JTAG1TDO : Test Data Out, input to BMC

JTAG1TDI : Test Data In, output from BMC

JTAG1TCK : Test Clock, output from BMC

JTAG1RTCK : Return Test Clock, input to BMC (if used)

## USB host

Interface has 1 USB host called USB2A. This is a differential pair named DP and DN, with two additional signals for USB Over Current Sense and USB VBUS control

USB Over Current Sense is to be used as follows:  Can be defined as over-current interrupt input from motherboard to detect if a USB device powered by the motherboard and attached to the BMC exceeds the specified current for the USB port.  Use of this signal is optional.

USB VBUS Control is to be used as follows:  Control over 5 V Bus that supplies power to the USB device (end-point).  In the case that the USB Device attached to the BMC enters an over-current state (as indicated by USB Over Current Sense) the BMC will de-assert this signal and 5 V supply to the USB device will go into a low voltage or low current state, such that the device will no longer have power.  Use of this signal is optional.

## USB device

Interface has 1 USB device called USB2B. This is a differential pair named DP and DN, with an additional signal VBUS, an analog pin

VBUS is intended to be used as follows:  Detects 5 V supply is asserted and allows the BMC to have its device port begin USB host negotiation.  Note that use of the 5 V supply detect is meant to indicate to the BMC as a device that a host is attached and supplying power.  Use of this signal is optional.

## SPI Master Interface for Firmware

The BMC boots from a flash memory device located on the Serial Peripheral Interface (SPI) bus. The device size is 256Mb (32MB) minimum and can be used to store FPGA,  CPLD , and miscellaneous recovery images. The device is Winbond W25Q256 or equivalent. A secondary device is supported to provide BMC recovery.  The daughterboard can have these onboard or utilize the secondary function signal pins over the connector if placement on the baseboard is mandatory.  Refer to Signal Priority and Nomenclature section of this specification.

## SPI Master Interface for Host

Two additional Serial Peripheral Interface (SPI) Master Controller interface signals are routed over the connector. Each bus has the capability of utilizing two chip selects used to select the primary or secondary SPI Flash device’s if used.

## LPC/eSPI

TODO:

## I2C

The interface features multiple I2C Bus compatible 2-wire interfaces consisting of a serial data line (SDA) and a serial clock line (SCL). If the daughterboard contains drives that are open-drain, the baseboard device shall require a pullup resistor to generate a logic high voltage and shall remain high even when the bus is idle. Proper power domain isolation shall be implemented on the daughterboard.  The AC/DC specifications are defined in the SMBus 2.0 and I2C bus specifications

TODO: do we pullup on the baseboard or do we pull up on the daughterboard. Refine spec and also mention

## UART

5 total UART interfaces are available to use. 3 UART interfaces are expected to be primary functioning and 2 are available if daughter board supports functionality. 1 UART is to be named CONSOLE for SOC console output if desired. The following summary lists the UART:

2 UART interfaces have secondary functional HW flow control signals such as CTS and RTS for a total of 4 pins. These are available to be used if desired but primary function is GPIO.

TODO: put table here to summarize.

## PWM

PWM output from BMC, meant to drive fans or pumps.  It is expected that these signals have whatever necessary level conversion before going over the interface.

## TACH

Tachometer input to BMC.  It is expected that these signals have whatever necessary level conversion before going over the interface.

## PECI

An Intel proprietary bus meant to read die temperature.  This defines two pins, PECI and PECIVDD.

PECI is a 1-wire data signal that acts as input to the BMC.

PECIVDD is the host voltage that defines a reference for the PECI interface.

Consult the Intel spec for more information.

## GPIO

Any GPIO is defined in the literal sense that it may be used for the purpose of defining an input or output signal to the BMC.  These are software configurable for use throughout the MB system as indicators, control pins, interrupts, and input logic read by the BMC

## SGPIO

SGPIO is the Serial GPIO interface.  The HW Interface describes a single Serial GPIO Master, though in some modules this may also act as a slave monitor.  There are four signals defined as master:

Master Serial GPIO Clock Output, controlling clock for the bus, output from the BMC.

Master Serial GPIO Serial Data Input, an input to the BMC.

Master Serial GPIO Serial Data Load, an output from the BMC.

Master Serial GPIO Serial Data Output, an output from the BMC.

## SCIPME

System Control Interrupt and Power Management.  This defines two pins that can be associated to special functionality related to interaction with the host

SIOONCTRL defines the interrupt controlled by the BMC to bring the host up.

SIOPME is the active low wake signal and is an ACPI interrupt.  Based on the particular module used there may be special logic behind the control of this pin.

## RESET

Input to the BMC, this pin will reset the BMC subsystem.

## WATCHDOG

## INDICATOR

This defines generic indication from the module to the system.  The use of this pin is dependent on the BMC module used, so consult specific documentation for that module.

## Reserved

## Pin Definition

The BMC daughter board shall have the following pinout:

Table 2 BMC connector/edge pinout

| Pin # | Name |  | Name | Pin # |
| --- | --- | --- | --- | --- |
| 1 | VDD_12V_STBY |  | VDD_1V8_STBY | 2 |
| 3 | VDD3_3V_STBY |  | VDD3_3V_STBY | 4 |
| 5 | VDD3_3V_STBY |  | VDD3_3V_STBY | 6 |
| 7 | VDD3_3V_STBY |  | GND | 8 |
| 9 | GND |  | DACG | 10 |
| 11 | GND |  | DACB | 12 |
| 13 | GPIO0_SGPMLD |  | DACR | 14 |
| 15 | GPIO1_SGPMI |  | VGAHS_GPIO2 | 16 |
| 17 | GPIO3_SGPMO |  | VGAVS_GPIO4 | 18 |
| 19 | GPIO5_SGPMCK |  | DDCCLK_GPIO6 | 20 |
| 21 | CONSOLERX |  | DDCDAT_GPIO8 | 22 |
| 23 | CONSOLETX |  | GND | 24 |
| 25 | GPIO7 |  | PWM0_GPIO10 | 26 |
| 27 | PWM2_GPIO9 |  | PWM1_GPIO12 | 28 |
| 29 | PWM4_GPIO11 |  | PWM3_GPIO14 | 30 |
| 31 | PWM6_GPIO13 |  | PWM5_GPIO16 | 32 |
| 33 | GND |  | PWM7_GPIO18 | 34 |
| 35 | GPIO15_UART1CTS |  | GPIO19 | 36 |
| 37 | GPIO17_UART1RTS |  | GPIO20_UART2CTS | 38 |
| 39 | GND |  | GPIO21_UART2RTS | 40 |
| 41 | UART1RX_GPIO23 |  | UART2RX_GPIO22 | 42 |
| 43 | UART1TX_GPIO25 |  | UART2TX_GPIO24 | 44 |
| 45 | GND |  | GPIO26 | 46 |
| 47 | I2C8SCL_GPIO27 |  | GPIO28_I2C13SCL | 48 |
| 49 | I2C8SDA_GPIO29 |  | GPIO30_I2C13SDA | 50 |
| 51 | GND |  | GND | 52 |
| 53 | I2C7SCL_GPIO31 |  | I2C6SCL_GPIO32 | 54 |
| 55 | I2C7SDA_GPIO33 |  | I2C6SDA_GPIO34 | 56 |
| 57 | GND |  | GND | 58 |
| 59 | GPIO35_FWSPIWP# |  | I2C5SCL_GPIO36 | 60 |
| 61 | GPIO37_INDICATOR# |  | I2C5SDA_GPIO38 | 62 |
| 63 | GPIO39_FWSPICS0# |  | GND | 64 |
| 65 | GPIO41_FWSPIMOSI_IO0 |  | GPIO40 | 66 |
| 67 | GPIO43_FWSPIMISO_IO1 |  | GPIO42 | 68 |
| 69 | GPIO45_FWSPI_IO2 |  | GPIO44 | 70 |
| 71 | GPIO47_FWSPI_IO3 |  | GPIO46 | 72 |
| 73 | GPIO49_FWSPICK |  | GPIO48 | 74 |
| 75 | GPIO51_FWSPICS1# |  | GPIO50 | 76 |
| 77 | PWRGD_GPIO53 |  | TACH0_GPIO52 | 78 |
| 79 | GPIO55 |  | TACH1_GPIO54 | 80 |
| 81 | GPIO57 |  | TACH2_GPIO56 | 82 |
| 83 | WDTRST2_GPIO59 |  | TACH3_GPIO58 | 84 |
| 85 | GPIO61 |  | TACH4_GPIO60 | 86 |
| 87 | SIOONCTRL#_GPIO63 |  | TACH5_GPIO62 | 88 |
| 89 | SIOPME#_GPIO65 |  | TACH6_GPIO64 | 90 |
| 91 | WDTRST1_GPIO67 |  | TACH7_GPIO66 | 92 |
| 93 | GPIO69 |  | TACH8_GPIO68 | 94 |
| 95 | GPIO71 |  | TACH9_GPIO70 | 96 |
| 97 | KLUDGE_GPIO73 |  | TACH10_GPIO72 | 98 |
| 99 | KLUDGE_GPIO75 |  | TACH11_GPIO74 | 100 |
| 101 | GPIO77 |  | TACH12_GPIO76 | 102 |
| 103 | GPIO79 |  | TACH13_GPIO78 | 104 |
| 105 | GPIO81 |  | TACH14_GPIO80 | 106 |
| 107 | GPIO83 |  | TACH15_GPIO82 | 108 |
| 109 | GPIO84 |  | GND | 110 |
| 111 | PECIVDD |  | PECI | 112 |
| 113 | GPIO85 |  | GND | 114 |
| 115 | GPIO87 |  | SPI2CK_GPIO86 | 116 |
| 117 | GPIO89 |  | SPI2MISO_GPIO88 | 118 |
| 119 | GPIO91 |  | SPI2MOSI_GPIO90 | 120 |
| 121 | GPIO93 |  | SPI2CS0#_GPIO92 | 122 |
| 123 | I2C2SCL_GPIO95 |  | SPI2CS1#_GPIO94 | 124 |
| 125 | I2C2SDA_GPIO97 |  | GND | 126 |
| 127 | GND |  | I2C1SCL_GPIO96 | 128 |
| 129 | GPIO99_I2C14SCL |  | I2C1SDA_GPIO98 | 130 |
| 131 | GPIO101_I2C14SDA |  | GND | 132 |
| 133 | GND |  | I2C4SCL_GPIO100 | 134 |
| 135 | GPIO103_I2C16SCL |  | I2C4SDA_GPIO102 | 136 |
| 137 | GPIO105_I2C16SDA |  | GPIO104 | 138 |
| 139 | GND |  | GPIO106 | 140 |
| 141 | I2C12SCL_GPIO107 |  | PERSTN | 142 |
| 143 | I2C12SDA_GPIO109 |  | GPIO108 | 144 |
|  | Mechanical Key |  |
| 145 | GND |  | GPIO110 | 146 |
| 147 | PERXN |  | GPIO111 | 148 |
| 149 | PERXP |  | GPIO112 | 150 |
| 151 | GND |  | BMCLPC3V3_BMCESPI1V8 | 152 |
| 153 | PETXN |  | GPIO113 | 154 |
| 155 | PETXP |  | GPIO114 | 156 |
| 157 | GND |  | GPIO115 | 158 |
| 159 | PEREFCLKN |  | GPIO116 | 160 |
| 161 | PEREFCLKP |  | JTAG1TRST | 162 |
| 163 | GND |  | JTAG1TDO | 164 |
| 165 | LPCRST#_ESPIRST# |  | JTAG1TDI | 166 |
| 167 | LPCD1_ESPID1 |  | JTAG1RTCK | 168 |
| 169 | LPCD0_ESPID0 |  | JTAG1TCK | 170 |
| 171 | LPCIRQ#_ESPIALERT# |  | JTAG1TMS | 172 |
| 173 | LPCFRAME#_ESPICS# |  | ADC0 | 174 |
| 175 | LPCD3_ESPID3 |  | ADC1 | 176 |
| 177 | LPCD2_ESPID2 |  | ADC2 | 178 |
| 179 | LPCCLK_ESPICLK |  | ADC3 | 180 |
| 181 | I2C9SCL_GPIO117 |  | ADC4 | 182 |
| 183 | I2C9SDA_GPIO119 |  | ADC5 | 184 |
| 185 | GND |  | ADC6 | 186 |
| 187 | I2C10SCL_GPIO121 |  | ADC7 | 188 |
| 189 | I2C10SDA_GPIO123 |  | SYSCS#_GPIO118 | 190 |
| 191 | GND |  | SYSMISO_GPIO120 | 192 |
| 193 | GPIO125_I2C15SCL |  | SYSMOSI_GPIO122 | 194 |
| 195 | GPIO127_I2C15SDA |  | SYSCK_GPIO124 | 196 |
| 197 | GND |  | SPI1CS0#_GPIO126 | 198 |
| 199 | I2C11SCL_GPIO129 |  | SPI1MOSI_GPIO128 | 200 |
| 201 | I2C11SDA_GPIO131 |  | SPI1MISO_GPIO130 | 202 |
| 203 | GND |  | GPIO132_SPI1_IO2 | 204 |
| 205 | I2C3SCL_GPIO133 |  | GPIO134_SPI1_IO3 | 206 |
| 207 | I2C3SDA_GPIO135 |  | SPI1CK_GPIO136 | 208 |
| 209 | GPIO137_USB2BVBUSSNS |  | SPI1CS1#_GPIO138 | 210 |
| 211 | GPIO139_USB2AVBUSSNS |  | GND | 212 |
| 213 | GPIO140_USB2APWREN |  | RMIIMDIO | 214 |
| 215 | GND |  | RMIICRSDV | 216 |
| 217 | USB2A_DN |  | RMIIMDC | 218 |
| 219 | USB2A_DP |  | RMIIRCLKI | 220 |
| 221 | GND |  | RMIIRXER | 222 |
| 223 | USB2B_DN |  | RMIITXEN | 224 |
| 225 | USB2B_DP |  | GND | 226 |
| 227 | GND |  | RMIIRXD0 | 228 |
| 229 | TRD0P_RGMIITXD0 |  | RMIIRXD1 | 230 |
| 231 | TRD0N_RGMIIRXD0 |  | GND | 232 |
| 233 | GND |  | RMIITXD0 | 234 |
| 235 | TRD1N_RGMIIRXD1 |  | RMIITXD1 | 236 |
| 237 | TRD1P_RGMIITXD1 |  | GND | 238 |
| 239 | GND |  | PHYLED1_RGMIITXCK | 240 |
| 241 | TRD2P_RGMIITXD2 |  | PHYLED2_RGMIIRXCTL | 242 |
| 243 | TRD2N_RGMIIRXD2 |  | PHYLED3_RGMIITXCTL | 244 |
| 245 | GND |  | GPIO141_RGMIIMDC | 246 |
| 247 | TRD3N_RGMIIRXD3 |  | GPIO142_RGMIIMDIO | 248 |
| 249 | TRD3P_RGMIITXD3 |  | GPIO143_RGMIIRXCK | 250 |
| 251 | GND |  | GPIO144_ADC8 | 252 |
| 253 | BMC_RESET# |  | GPIO146_ADC9 | 254 |
| 255 | GPIO145_ADC11 |  | GPIO148_ADC10 | 256 |
| 257 | GPIO147_ADC13 |  | GPIO150_ADC12 | 258 |
| 259 | GPIO149_ADC15 |  | GPIO151_ADC14 | 260 |

## Signal Priority and Nomenclature

The BMC pinout specification allows for primary and secondary functionality to provide flexibility to the system designer. If SOC’s do not support multiplexing, it will be assumed primary function is dominant.

Table 3 BMC primary and secondary conventions

| Subsystem | Net Name | Primary | Secondary | Direction | Description Primary | Description Secondary |
| --- | --- | --- | --- | --- | --- | --- |
| 1 GbT/RGMII/GPIO | GPIO_RGMIIRXCK | GPIO | RGMIIRXCK | BI | GPIO | RGMII 2 receive clock |
| 1 GbT/RGMII/GPIO | PHYLED1_RGMIITXCK | PHYLED1 | RGMIITXCK | BI | GPIO intended for MAGJACK LEDs, or signal from PHY | RGMII 2 transmit clock |
| 1 GbT/RGMII/GPIO | PHYLED2_RGMIIRXCTL | PHYLED2 | RGMIIRXCTL | BI | GPIO intended for MAGJACK LEDs, or signal from PHY | RGMII 2 receive control |
| 1 GbT/RGMII/GPIO | PHYLED3_RGMIITXCTL | PHYLED3 | RGMIITXCTL | BI | GPIO intended for MAGJACK LEDs, or signal from PHY | RGMII 2 transmit control |
| 1 GbT/RGMII/GPIO | GPIO_RGMIIMDC | GPIO | RGMIIMDC | O | GPIO | Management Data Clock. The MDC clock input must be provided to allow MII management functions. |
| 1 GbT/RGMII/GPIO | GPIO_RGMIIMDIO | GPIO | RGMIIMDIO | BI | GPIO | Management Data I/O. This serial input/output bit is used to read from and write to the MII registers |
| 1 GbT/RGMII/GPIO | TRD0N_RGMIIRXD0 | TRD0N | RGMIIRXD0 | BI | Transmit/Receive Pair 0 | RGMII 2 receive data bus from PHY bit 0 |
| 1 GbT/RGMII/GPIO | TRD0P_RGMIITXD0 | TRD0P | RGMIITXD0 | BI | Transmit/Receive Pair 0 | RGMII 2 transmit data bus to PHY bit 0 |
| 1 GbT/RGMII/GPIO | TRD1N_RGMIIRXD1 | TRD1N | RGMIIRXD1 | BI | Transmit/Receive Pair 1 | RGMII 2 receive data bus from PHY bit 1 |
| 1 GbT/RGMII/GPIO | TRD1P_RGMIITXD1 | TRD1P | RGMIITXD1 | BI | Transmit/Receive Pair 1 | RGMII 2 transmit data bus to PHY bit 1 |
| 1 GbT/RGMII/GPIO | TRD2N_RGMIIRXD2 | TRD2N | RGMIIRXD2 | BI | Transmit/Receive Pair 2 | RGMII 2 receive data bus from PHY bit 2 |
| 1 GbT/RGMII/GPIO | TRD2P_RGMIITXD2 | TRD2P | RGMIITXD2 | BI | Transmit/Receive Pair 2 | RGMII 2 transmit data bus to PHY bit 2 |
| 1 GbT/RGMII/GPIO | TRD3N_RGMIIRXD3 | TRD3N | RGMIIRXD3 | BI | Transmit/Receive Pair 3 | RGMII 2 receive data bus from PHY bit 3 |
| 1 GbT/RGMII/GPIO | TRD3P_RGMIITXD3 | TRD3P | RGMIITXD3 | BI | Transmit/Receive Pair 3 | RGMII 2 transmit data bus to PHY bit 3 |
| 1.8V | VDD_1V8_STBY | VDD_1V8_STBY |  |  | 1.8v supply to PCB | none |
| 12v | VDD_12V_STBY | VDD_12V_STBY |  |  | 12v supply to PCB | none |
| 3.3V | VDD3_3V_STBY | VDD3_3V_STBY |  |  | 3.3v supply to PCB | none |
| 3.3V | VDD3_3V_STBY | VDD3_3V_STBY |  |  | 3.3v supply to PCB | none |
| 3.3V | VDD3_3V_STBY | VDD3_3V_STBY |  |  | 3.3v supply to PCB | none |
| 3.3V | VDD3_3V_STBY | VDD3_3V_STBY |  |  | 3.3v supply to PCB | none |
| 3.3V | VDD3_3V_STBY | VDD3_3V_STBY |  |  | 3.3v supply to PCB | none |
| 3.3Vlpc or 1.8espi | BMCLPC3V3_BMCeSPI1v8 | BMCLPC3V3 | BMCeSPI1v8 |  | 3.3v supply to PCB LPC/eSPI | 1.8v supply if needed for eSPI |
| ADC | ADC0 | ADC0 |  | INPUT | channel 0 analog input |  |
| ADC | ADC1 | ADC1 |  | INPUT | channel 1 analog input |  |
| ADC | ADC2 | ADC2 |  | INPUT | channel 2 analog input |  |
| ADC | ADC3 | ADC3 |  | INPUT | channel 3 analog input |  |
| ADC | ADC4 | ADC4 |  | INPUT | channel 4 analog input |  |
| ADC | ADC5 | ADC5 |  | INPUT | channel 5 analog input |  |
| ADC | ADC6 | ADC6 |  | INPUT | channel 6 analog input |  |
| ADC | ADC7 | ADC7 |  | INPUT | channel 7 analog input |  |
| ADC/GPIO | GPIO_ADC10 | GPIO | ADC10 | INPUT | GPIO | channel 10 analog input |
| ADC/GPIO | GPIO_ADC11 | GPIO | ADC11 | INPUT | GPIO | channel 11 analog input |
| ADC/GPIO | GPIO_ADC12 | GPIO | ADC12 | INPUT | GPIO | channel 12 analog input |
| ADC/GPIO | GPIO_ADC13 | GPIO | ADC13 | INPUT | GPIO | channel 13 analog input |
| ADC/GPIO | GPIO_ADC14 | GPIO | ADC14 | INPUT | GPIO | channel 14 analog input |
| ADC/GPIO | GPIO_ADC15 | GPIO | ADC15 | INPUT | GPIO | channel 15 analog input |
| ADC/GPIO | GPIO_ADC8 | GPIO | ADC8 | INPUT | GPIO | channel 8 analog input |
| ADC/GPIO | GPIO_ADC9 | GPIO | ADC9 | INPUT | GPIO | channel 9 analog input |
| FWSPI | GPIO_FWSPICK | GPIO | FWSPICK |  | GPIO | BMC FW clock output for FW living on MB |
| FWSPI | GPIO_FWSPICS0# | GPIO | FWSPICS0# |  | GPIO | BMC FW chip select 0 for FW living on MB |
| FWSPI | GPIO_FWSPICS1# | GPIO | FWSPICS1# |  | GPIO | BMC FW chip select 1 for FW living on MB |
| FWSPI | GPIO_FWSPIMISO_IO1 | GPIO | FWSPIMISO_IO1 |  | GPIO | BMC FW MISO/IO0 for FW living on MB |
| FWSPI | GPIO_FWSPIMOSI_IO0 | GPIO | FWSPIMOSI_IO0 |  | GPIO | BMC FW MOSI/IO1 for FW living on MB |
| FWSPI | GPIO_FWSPI_IO2 | GPIO | FWSPI_IO2 |  | GPIO | BMC FW IO2 for FW living on MB to support quad |
| FWSPI | GPIO_FWSPI_IO3 | GPIO | FWSPI_IO3 |  | GPIO | BMC FW IO3 for FW living on MB to support quad |
| GND | GND | GND |  |  | GND |  |
| GND | GND | GND |  |  | GND |  |
| GND | GND | GND |  |  | GND |  |
| GND | GND | GND |  |  | GND |  |
| GND | GND | GND |  |  | GND |  |
| GND | GND | GND |  |  | GND |  |
| GND | GND | GND |  |  | GND |  |
| GND | GND | GND |  |  | GND |  |
| GND | GND | GND |  |  | GND |  |
| GND | GND | GND |  |  | GND |  |
| GND | GND | GND |  |  | GND |  |
| GND | GND | GND |  |  | GND |  |
| GND | GND | GND |  |  | GND |  |
| GND | GND | GND |  |  | GND |  |
| GND | GND | GND |  |  | GND |  |
| GND | GND | GND |  |  | GND |  |
| GND | GND | GND |  |  | GND |  |
| GND | GND | GND |  |  | GND |  |
| GND | GND | GND |  |  | GND |  |
| GND | GND | GND |  |  | GND |  |
| GND | GND | GND |  |  | GND |  |
| GND | GND | GND |  |  | GND |  |
| GND | GND | GND |  |  | GND |  |
| GND | GND | GND |  |  | GND |  |
| GND | GND | GND |  |  | GND |  |
| GND | GND | GND |  |  | GND |  |
| GND | GND | GND |  |  | GND |  |
| GND | GND | GND |  |  | GND |  |
| GND | GND | GND |  |  | GND |  |
| GND | GND | GND |  |  | GND |  |
| GND | GND | GND |  |  | GND |  |
| GND | GND | GND |  |  | GND |  |
| GND | GND | GND |  |  | GND |  |
| GND | GND | GND |  |  | GND |  |
| GND | GND | GND |  |  | GND |  |
| GND | GND | GND |  |  | GND |  |
| GND | GND | GND |  |  | GND |  |
| GND | GND | GND |  |  | GND |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| GPIO | GPIO | GPIO |  |  | GPIO |  |
| I2C | I2C10SCL_GPIO | I2C10SCL | GPIO |  | I2C/SMBUS 10 clock | GPIO |
| I2C | I2C10SDA_GPIO | I2C10SDA | GPIO |  | I2C/SMBUS 10 data | GPIO |
| I2C | I2C11SCL_GPIO | I2C11SCL | GPIO |  | I2C/SMBUS 11 clock | GPIO |
| I2C | I2C11SDA_GPIO | I2C11SDA | GPIO |  | I2C/SMBUS 11 data | GPIO |
| I2C | I2C12SCL_GPIO | I2C12SCL | GPIO |  | I2C/SMBUS 12 clock | GPIO |
| I2C | I2C12SDA_GPIO | I2C12SDA | GPIO |  | I2C/SMBUS 12 data | GPIO |
| I2C | I2C1SCL_GPIO | I2C1SCL | GPIO |  | I2C/SMBUS 1 clock | GPIO |
| I2C | I2C1SDA_GPIO | I2C1SDA | GPIO |  | I2C/SMBUS 1 data | GPIO |
| I2C | I2C2SCL_GPIO | I2C2SCL | GPIO |  | I2C/SMBUS 2 clock | GPIO |
| I2C | I2C2SDA_GPIO | I2C2SDA | GPIO |  | I2C/SMBUS 2 data | GPIO |
| I2C | I2C3SCL_GPIO | I2C3SCL | GPIO |  | I2C/SMBUS 3 clock | GPIO |
| I2C | I2C3SDA_GPIO | I2C3SDA | GPIO |  | I2C/SMBUS 3 data | GPIO |
| I2C | I2C4SCL_GPIO | I2C4SCL | GPIO |  | I2C/SMBUS 4 clock | GPIO |
| I2C | I2C4SDA_GPIO | I2C4SDA | GPIO |  | I2C/SMBUS 4 data | GPIO |
| I2C | I2C5SCL_GPIO | I2C5SCL | GPIO |  | I2C/SMBUS 5 clock | GPIO |
| I2C | I2C5SDA_GPIO | I2C5SDA | GPIO |  | I2C/SMBUS 5 data | GPIO |
| I2C | I2C6SCL_GPIO | I2C6SCL | GPIO |  | I2C/SMBUS 6 clock | GPIO |
| I2C | I2C6SDA_GPIO | I2C6SDA | GPIO |  | I2C/SMBUS 6 data | GPIO |
| I2C | I2C7SCL_GPIO | I2C7SCL | GPIO |  | I2C/SMBUS 7 clock | GPIO |
| I2C | I2C7SDA_GPIO | I2C7SDA | GPIO |  | I2C/SMBUS 7 data | GPIO |
| I2C | I2C8SCL_GPIO | I2C8SCL | GPIO |  | I2C/SMBUS 8 clock | GPIO |
| I2C | I2C8SDA_GPIO | I2C8SDA | GPIO |  | I2C/SMBUS 8 data | GPIO |
| I2C | I2C9SCL_GPIO | I2C9SCL | GPIO |  | I2C/SMBUS 9 clock | GPIO |
| I2C | I2C9SDA_GPIO | I2C9SDA | GPIO |  | I2C/SMBUS 9 data | GPIO |
| I2C | GPIO_I2C13SCL | GPIO | I2C13SCL |  | GPIO | I2C/SMBUS 13 clock |
| I2C | GPIO_I2C13SDA | GPIO | I2C13SDA |  | GPIO | I2C/SMBUS 13 data |
| I2C | GPIO_I2C14SCL | GPIO | I2C14SCL |  | GPIO | I2C/SMBUS 14 clock |
| I2C | GPIO_I2C14SDA | GPIO | I2C14SDA |  | GPIO | I2C/SMBUS 14 data |
| I2C | GPIO_I2C15SCL | GPIO | I2C15SCL |  | GPIO | I2C/SMBUS 15 clock |
| I2C | GPIO_I2C15SDA | GPIO | I2C15SDA |  | GPIO | I2C/SMBUS 15 data |
| I2C | GPIO_I2C16SCL | GPIO | I2C16SCL |  | GPIO | I2C/SMBUS 16 clock |
| I2C | GPIO_I2C16SDA | GPIO | I2C16SDA |  | GPIO | I2C/SMBUS 16 data |
| INDICATOR | GPIO_INDICATOR | GPIO | INDICATOR | OUTPUT | Boot indication from BMC / GPIO option | GPIO |
| JTAG | JTAG1RTCK | JTAG1RTCK |  |  | JTAG Return Test Clock |  |
| JTAG | JTAG1TCK | JTAG1TCK |  |  | JTAG Test Clock |  |
| JTAG | JTAG1TDI | JTAG1TDI |  |  | JTAG Test Data In |  |
| JTAG | JTAG1TDO | JTAG1TDO |  |  | JTAG Test Data Out |  |
| JTAG | JTAG1TMS | JTAG1TMS |  |  | JTAG Test Mode Select |  |
| JTAG | JTAG1TRST | JTAG1TRST |  |  | JTAG Test Reset |  |
| LPC/eSPI | LPCCLK_ESPICLK | LPCCLK | ESPICLK |  | LPC bus clock input (default) | eSPI clock input |
| LPC/eSPI | LPCD0_ESPID0 | LPCD0 | ESPID0 |  | LPC address and data bus bit 0 | eSPI data bus bit 0 |
| LPC/eSPI | LPCD1_ESPID1 | LPCD1 | ESPID1 |  | LPC address and data bus bit 1 | eSPI data bus bit 1 |
| LPC/eSPI | LPCD2_ESPID2 | LPCD2 | ESPID2 |  | LPC address and data bus bit 2 | eSPI data bus bit 2 |
| LPC/eSPI | LPCD3_ESPID3 | LPCD3 | ESPID3 |  | LPC address and data bus bit 3 | eSPI data bus bit 3 |
| LPC/eSPI | LPCFRAME#_ESPICS# | LPCFRAME# | ESPICS# |  | LPC FRAME# (default) | eSPI chip select input |
| LPC/eSPI | LPCIRQ#_ESPIALERT# | LPCIRQ# | ESPIALERT# |  | LPC serial IRQ (default) | eSPI Alert |
| LPC/eSPI | LPCRST#_ESPIRST# | LPCRST# | ESPIRST# |  | LPC reset input (default) | eSPI reset input |
| PCIE | PEREFCLKN | PEREFCLKN |  | INPUT | PCI Express Reference clock input, 100MHz negative input of the differential clock pair | none |
| PCIE | PEREFCLKP | PEREFCLKP |  | INPUT | PCI Express Reference clock input, 100MHz positive input of the differential clock pair | none |
| PCIE | PERSTN | PERSTN |  | OUTPUT | PCI Express reset pin This reset signal reset PCI Express bus controller and VGA/2D device. | none |
| PCIE | PERXN | PERXN |  | INPUT | PCI Express Serial Data Receiver It receives negative input of the differential signal pair. | none |
| PCIE | PERXP | PERXP |  | INPUT | PCI Express Serial Data Receiver It receives positive input of the differential signal pair. | none |
| PCIE | PETXN | PETXN |  | OUTPUT | PCI Express Serial Data Transmitter It transmits negative output of the differential signal pa | none |
| PCIE | PETXP | PETXP |  | OUTPUT | PCI Express Serial Data Transmitter It transmits positive output of the differential signal pair. | none |
| PECI | PECI | PECI |  |  | PECI signal input to BMC | none |
| PECI | PECIVDD | PECIVDD |  |  | PECI power | none |
| PWM/GPIO | PWM0_GPIO | PWM0 | GPIO |  | PWM output | GPIO |
| PWM/GPIO | PWM1_GPIO | PWM1 | GPIO |  | PWM output | GPIO |
| PWM/GPIO | PWM2_GPIO | PWM2 | GPIO |  | PWM output | GPIO |
| PWM/GPIO | PWM3_GPIO | PWM3 | GPIO |  | PWM output | GPIO |
| PWM/GPIO | PWM4_GPIO | PWM4 | GPIO |  | PWM output | GPIO |
| PWM/GPIO | PWM5_GPIO | PWM5 | GPIO |  | PWM output | GPIO |
| PWM/GPIO | PWM6_GPIO | PWM6 | GPIO |  | PWM output | GPIO |
| PWM/GPIO | PWM7_GPIO | PWM7 | GPIO |  | PWM output | GPIO |
| RESET | BMC_RESET# | BMC_RESET# |  | INPUT | Core Reset circuitry for SOC and any periphery components needed for reset |  |
| RESET | PWRGD | PWRGD |  | INPUT | power Good from power supply |  |
| RFU | KLUDGE_GPIO | KLUDGE | GPIO |  | Kludge pins | GPIO |
| RFU | KLUDGE_GPIO | KLUDGE | GPIO |  | Kludge pins | GPIO |
| RMII | RMIICRSDV | RMIICRSDV |  |  | RMII/NCSI 1 receive carrier sense and data valid |  |
| RMII | RMIIMDC | RMIIMDC |  |  | Management Data Clock. The MDC clock input must be provided to allow MII management functions. |  |
| RMII | RMIIMDIO | RMIIMDIO |  |  | Management Data I/O. This serial input/output bit is used to read from and write to the MII registers |  |
| RMII | RMIIRCLKI | RMIIRCLKI |  |  | RMII/NCSI 1 50MHz reference clock input |  |
| RMII | RMIIRXD0 | RMIIRXD0 |  |  | RMII/NCSI 1 receive data bus from PHY bit 0 |  |
| RMII | RMIIRXD1 | RMIIRXD1 |  |  | RMII/NCSI 1 receive data bus from PHY bit 1 |  |
| RMII | RMIIRXER | RMIIRXER |  |  | RMII/NCSI 1 receive data error |  |
| RMII | RMIITXD0 | RMIITXD0 |  |  | RMII/NCSI 1 transmit data bus to PHY bit 0 |  |
| RMII | RMIITXD1 | RMIITXD1 |  |  | RMII/NCSI 1 transmit data bus to PHY bit 1 |  |
| RMII | RMIITXEN | RMIITXEN |  |  | RMII/NCSI 1 transmit enable |  |
| SGPIO/GPIO | GPIO_SGPMCK | GPIO | SGPMCK |  | GPIO | Master Serial GPIO clock output |
| SGPIO/GPIO | GPIO_SGPMI | GPIO | SGPMI |  | GPIO | Master Serial GPIO serial data input |
| SGPIO/GPIO | GPIO_SGPMLD | GPIO | SGPMLD |  | GPIO | Master Serial GPIO serial data load output |
| SGPIO/GPIO | GPIO_SGPMO | GPIO | SGPMO |  | GPIO | Master Serial GPIO serial data output |
| SIO/GPIO | SIOONCTRL#_GPIO | SIOONCTRL# | GPIO | OUTPUT | GPIO | System Control Interrupt/Power Managment. Power supply control switch (active low). It is software controlled GPIO usually for a BMC. |
| SIO/GPIO | SIOPME#_GPIO | SIOPME# | GPIO |  | GPIO | Active low wake signal and ACPI interrupt combined signal. It can be by SW controlled GPIO, but in Poleg BMC we have some logic behind it, so we would like to have a dedicated pin. |
| SPI/GPIO | SPI1MISO_IO1_GPIO | SPI1MISO_IO1 | GPIO |  | SPI 1 MOSI/IO1 | GPIO |
| SPI/GPIO | SPI1MOSI_IO0_GPIO | SPI1MOSI_IO0 | GPIO |  | SPI 1 MISO/IO0 | GPIO |
| SPI/GPIO | SPI1CK_GPIO | SPI1CK | GPIO |  | SPI 1 clock output | GPIO |
| SPI/GPIO | SPI1CS0#_GPIO | SPI1CS0# | GPIO |  | SPI 1 chip select 0 | GPIO |
| SPI/GPIO | SPI1CS1#_GPIO | SPI1CS1# | GPIO |  | SPI 1 chip select 1 | GPIO |
| SPI/GPIO | GPIO_SPI1_IO2 | GPIO | SPI1_IO2 |  | GPIO | SPI1 IO2 to support quad |
| SPI/GPIO | GPIO_SPI1_IO3 | GPIO | SPI1_IO3 |  | GPIO | SPI1 IO3 to support quad |
| SPI/GPIO | SPI2CK_GPIO | SPI2CK | GPIO |  | SPI 2 clock output | GPIO |
| SPI/GPIO | SPI2CS0#_GPIO | SPI2CS0# | GPIO |  | SPI 2 chip select 0 | GPIO |
| SPI/GPIO | SPI2CS1#_GPIO | SPI2CS1# | GPIO |  | SPI 2 chip select 1 | GPIO |
| SPI/GPIO | SPI2MISO_GPIO | SPI2MISO | GPIO |  | SPI 2 MISO | GPIO |
| SPI/GPIO | SPI2MOSI_GPIO | SPI2MOSI | GPIO |  | SPI 2 MOSI | GPIO |
| TACH/GPIO | TACH0_GPIO | TACH0 | GPIO |  | Fan Tachometer input | GPIO |
| TACH/GPIO | TACH1_GPIO | TACH1 | GPIO |  | Fan Tachometer input | GPIO |
| TACH/GPIO | TACH10_GPIO | TACH10 | GPIO |  | Fan Tachometer input | GPIO |
| TACH/GPIO | TACH11_GPIO | TACH11 | GPIO |  | Fan Tachometer input | GPIO |
| TACH/GPIO | TACH12_GPIO | TACH12 | GPIO |  | Fan Tachometer input | GPIO |
| TACH/GPIO | TACH13_GPIO | TACH13 | GPIO |  | Fan Tachometer input | GPIO |
| TACH/GPIO | TACH14_GPIO | TACH14 | GPIO |  | Fan Tachometer input | GPIO |
| TACH/GPIO | TACH15_GPIO | TACH15 | GPIO |  | Fan Tachometer input | GPIO |
| TACH/GPIO | TACH2_GPIO | TACH2 | GPIO |  | Fan Tachometer input | GPIO |
| TACH/GPIO | TACH3_GPIO | TACH3 | GPIO |  | Fan Tachometer input | GPIO |
| TACH/GPIO | TACH4_GPIO | TACH4 | GPIO |  | Fan Tachometer input | GPIO |
| TACH/GPIO | TACH5_GPIO | TACH5 | GPIO |  | Fan Tachometer input | GPIO |
| TACH/GPIO | TACH6_GPIO | TACH6 | GPIO |  | Fan Tachometer input | GPIO |
| TACH/GPIO | TACH7_GPIO | TACH7 | GPIO |  | Fan Tachometer input | GPIO |
| TACH/GPIO | TACH8_GPIO | TACH8 | GPIO |  | Fan Tachometer input | GPIO |
| TACH/GPIO | TACH9_GPIO | TACH9 | GPIO |  | Fan Tachometer input | GPIO |
| UART | CONSOLERX_GPIO | CONSOLERX | GPIO |  | receive serial data input, primary console |  |
| UART | CONSOLETX_GPIO | CONSOLETX | GPIO |  | transmit serial data output, primary console |  |
| UART | UART1TX_GPIO | UART1TX | GPIO |  | receive serial data input |  |
| UART | UART1RX_GPIO | UART1RX | GPIO |  | transmit serial data output |  |
| UART | UART2TX_GPIO | UART2TX | GPIO |  | receive serial data input |  |
| UART | UART2RX_GPIO | UART2RX | GPIO |  | transmit serial data output |  |
| UART_Flow | GPIO_UART2CTS | GPIO | UART2CTS |  | GPIO | Clear to send modem status |
| UART_Flow | GPIO_UART2RTS | GPIO | UART2RTS |  | GPIO | Request to send modem status |
| UART_Flow | GPIO_UART1CTS | GPIO | UART1CTS |  | GPIO | Clear to send modem status |
| UART_Flow | GPIO_UART1RTS | GPIO | UART1RTS |  | GPIO | Request to send modem status |
| USB | USB2A_DN | USB2A_DN |  |  | D− signal of USB 2.0 port A, USB host/device |  |
| USB | USB2A_DP | USB2A_DP |  |  | D+ signal of USB 2.0 port A, USB host/device |  |
| USB | GPIO_USB2AVBUSOVC | GPIO | USB2AVBUSOVC |  | Host/device Overcurrent sense | GPIO |
| USB | GPIO_USB2AVBUSC | GPIO | USB2AVBUSC |  | Host/device VBUS Control | GPIO |
| USB | USB2B_DN | USB2B_DN |  |  | D− signal of USB 2.0 port B, device |  |
| USB | USB2B_DP | USB2B_DP |  |  | D+ signal of USB 2.0 port B, device |  |
| USB | GPIO_USB2BVBUSSNS | GPIO | USB2BVBUSSNS |  | Device VBUS Sense | GPIO |
| VGA | DACB | DACB |  | O | DAC B channel output |  |
| VGA | DACG | DACG |  | O | DAC G channel output |  |
| VGA | DACR | DACR |  | O | DAC R channel output |  |
| VGA | DDCCLK_GPIO | DDCCLK | GPIO | I/O | VGA DDC clock pin | GPIO |
| VGA | DDCDAT_GPIO | DDCDAT | GPIO | I/O | VGA DDC data pin | GPIO |
| VGA | VGAHS_GPIO | VGAHS | GPIO | I/O | VGA horizontal sync output | GPIO |
| VGA | VGAVS_GPIO | VGAVS | GPIO | I/O | VGA vertical sync output | GPIO |
| WATCHDOG/GPIO | WDTRST1_GPIO | WDTRST1 | GPIO | OUTPUT | Watchdog timer 1 timeout pulse output | GPIO |
| WATCHDOG/GPIO | WDTRST2_GPIO | WDTRST2 | GPIO | OUTPUT | Watchdog timer 2 timeout pulse output | GPIO |

# Power

## Electrical Requirements

Connector Electrical Requirements shall meet PS-003A-01 JEDEC specification.

| DC Electrical Requirements | Requirement |  |
| --- | --- | --- |
| Current carrying capability at 30 °C temperature rise per contact | 0.50 amp/pin De-rated |  |

| Power and Ground Requirements | Pin Count | Description | Maximum Current/Power |
| --- | --- | --- | --- |
| VDD_12V_STBY | 1 | +12V main or +12v aux | .5amps/6watts |
| VDD3_3V_STBY | 5 | +3.3V main or +3.3 aux | .5amps/8.25watts |
| VDD_1V8_STBY | 1 | LPC or eSPI voltage reference | For reference only |
| GND | 38 | Ground Return |  |

# Mechanical

## Form Factor

The BMC module shall conform to the 260 Pin DDR4 SODIMM, .50mm Pitch DIMM Registration form factor, defined by MO-310C.  The module has a 260 pin edge connector. Refer to JEDEC spec for dimensions, tolerances, and height restrictions. (SFDC to discuss if we should relax component width keepout from 3.7mm to 5mm/TBD)

Figure 5-1 BMC Form Factor

The 260 pin edge connector is .5 mm pitch (+/-0.03), and is 1.20mm (+/-0.1) thick. The PCB edge connector contacts shall be gold plated per JEDEC spec.

| Figure 5-2 BMC Thickness | Figure 5-3 BMC pin pitch |
| --- | --- |

## Mating Connector

The BMC mating connector shall conform to the DDR4 Small Outline Dual Inline Memory Module (SODIMM), 260 pin, 0.50 mm pitch Socket Outline, defined by SO-018D.

A conforming vertical connector, Amphenol G634B2610X22HR, or equivalent can be mounted on the motherboard or network device, to mate with the BMC module edge connector. Right Angle or Angled connectors are permissible if conformant to SO-18D specification.

# Thermal

The BMC mezzanine card can be located in any position of the server or network motherboard. The worst-case environmental conditions can be expected to be (SFDC TO FILL OUT). The thermal solution, component selections, and design should consider for these conditions.

TBD CHART to show Operating Conditions

# References

- Registration - 260 Pin DDR4 SODIMM, 0.50 mm Pitch. DIMM; M0-310C, Item No. 11-14-164

- Registration - DDR4 Small Outline Dual Inline Memory Module (SODIMM), 260 pin, 0.50 mm pitch Socket Outline; SO-018D, Item No. 14-180

- NXP Semiconductors. I2C-bus specification and user manual. NXP Semiconductors, Rev 6, April 4th, 2014.