Rack-Busbar interface

02

Author: D.P.Winsor

# License

Contributions to this Specification are made under the terms and conditions set forth in Open Web Foundation Contributor License Agreement (“OWF CLA 1.0”) (“Contribution License”) by:

Derek Paul Winsor, Rittal.

You can review the signed copies of the applicable Contributor License(s) for this Specification on the OCP website at http://www.opencompute.org/products/specsanddesign

Usage of this Specification is governed by the terms and conditions set forth in Open Web Foundation Final Specification Agreement (“OWFa 1.0”), Open Compute Project Hardware License – Permissive (“OCPHL Permissive”), You can review the applicable Specification License(s) executed by the above referenced contributors to this Specification on the OCP website at http://www.opencompute.org/participate/legal-documents/

Note:  The following clarifications, which distinguish technology licensed in the Contribution License and/or Specification License from those technologies merely referenced (but not licensed),  were accepted by the Incubation Committee of the OCP:

None

NOTWITHSTANDING THE FOREGOING LICENSES, THIS SPECIFICATION IS PROVIDED BY OCP "AS IS" AND OCP EXPRESSLY DISCLAIMS ANY WARRANTIES (EXPRESS, IMPLIED, OR OTHERWISE), INCLUDING IMPLIED WARRANTIES OF MERCHANTABILITY, NON-INFRINGEMENT, FITNESS FOR A PARTICULAR PURPOSE, OR TITLE, RELATED TO THE SPECIFICATION. NOTICE IS HEREBY GIVEN, THAT OTHER RIGHTS NOT GRANTED AS SET FORTH ABOVE, INCLUDING WITHOUT LIMITATION, RIGHTS OF THIRD PARTIES WHO DID NOT EXECUTE THE ABOVE LICENSES, MAY BE IMPLICATED BY THE IMPLEMENTATION OF OR COMPLIANCE WITH THIS SPECIFICATION. OCP IS NOT RESPONSIBLE FOR IDENTIFYING RIGHTS FOR WHICH A LICENSE MAY BE REQUIRED IN ORDER TO IMPLEMENT THIS SPECIFICATION.  THE ENTIRE RISK AS TO IMPLEMENTING OR OTHERWISE USING THE SPECIFICATION IS ASSUMED BY YOU. IN NO EVENT WILL OCP BE LIABLE TO YOU FOR ANY MONETARY DAMAGES WITH RESPECT TO ANY CLAIMS RELATED TO, OR ARISING OUT OF YOUR USE OF THIS SPECIFICATION, INCLUDING BUT NOT LIMITED TO ANY LIABILITY FOR LOST PROFITS OR ANY CONSEQUENTIAL, INCIDENTAL, INDIRECT, SPECIAL OR PUNITIVE DAMAGES OF ANY CHARACTER FROM ANY CAUSES OF ACTION OF ANY KIND WITH RESPECT TO THIS SPECIFICATION, WHETHER BASED ON BREACH OF CONTRACT, TORT (INCLUDING NEGLIGENCE), OR OTHERWISE, AND EVEN IF OCP HAS BEEN ADVISED OF THE POSSIBILITY OF SUCH DAMAGE.

Table of Contents

1.	License	2

Table of Contents	3

2.	Scope	4

Overview	5

3.	Busbsar definition	6

4.	Physical Specifications	7

4.1	Rack interface Bottom.	7

4.2	Rack interface Top.	9

4.3	Busbar interface Bottom	11

4.4	Busbar interface Top.	12

4.5	Busbar Upper location feature.	13

4.6	Busbar upper location jig.	13

4.7	Busbar overall height	15

4.8	Busbar support	15

4.9	Half height busbar	16

5.	Busbar support brace	16

6.	Mechanical fixing, Busbar to rack.	17

# Scope

This document defines the technical specifications for the Busbar assembly to Rack interface for the Open Compute Project Rack and Power Enclosure, to ensure the interface remains the standard across all platforms for all variants of Busbars.

# Overview

The technical requirements for the Busbar are still contained within the Open Rack Standard. This specification defines the interface of the Busbar assembly to the Rack, in order to consistently achieve the requirements laid down in the Open Rack Standard across 12V/48V busbars. This enables Busbars to be retro fitted; upgraded for different power capability or swapped from 12V to 48V on a common rack interface, ensuring a robust supply chain where products are interchangeable across Vendors platforms and orderable as a recognized SKU throughout the community.

# Busbsar definition

To clarify busbar specification a generic part numbering system is applied and defined as follows:

BBOCP-12-AA-BBB-CCCC-DD-PSEEFF

Busbar part number format

Sections are broken down as follows:

BBOCP remains consistent and identifies part as ‘Busbar for OCP product’.

12: identifies the required Voltage, i.e. 48V.

AA: identifies the required power rating per Busbar, per zone i.e. 09 for 9kw

BBB: identifies rack height, 42 for 42OU rack, F for full height, H for half height, i.e. 42F

CCCC: Identifies support brace position and split in power zones (if needed), above this OU, i.e. 19 (brace is fitted above this OU space), so single busbar support would be classed as 1900. Where a twin busbar support could be classed as 0339 (one above 3OU and above 39OU), note:

DD: Identifies space between OU in millimetres where Rack brace is fitted. If two Busbar support braces are being used i.e. CCCC = 0339, the position for the second brace from the centre of first brace, would be number of OU difference +DD. So if DD is 28 and CCCC is 0339, then 36OUx48mm+28mm =1756mm fixing centres.

PSEEFF: identifies the Powershelf connection location i.e. PS0928 where:

PS: remains constant

EE: position where first Powershelf connects to Busbar in OU i.e 09

FF:  position where second Powershelf connects to Busbar in OU i.e. 00 if none req.

So from above BBOCP-12-09-42F-1900-00-PS0900

Defines a 12V Bubsar for 9kW, 42OU Full height with no central rack brace but with busbar brace fitted above 19OU with one Powershelf connected at 9OU.

BBOCP-12-07-42F-1900-28-PS0928

Defines a 12V Busbar for 7kW, 42OU Full height with 28mm central rack brace where zones split above 19OU, with two Power zones, one shelf fitted at 9OU; the other fitted at 28OU.

This part number must be displayed on the Busbar cage assembly.

Assumptions:

OU starts from the base of the rack

Specification is based on maximum height 42OU rack with 2059mm between face of base to face of canopy interface. For other heights add/subtract OU from this dimension, i.e. for 44OU height rack: 44OU-42OU=2OU difference, 2x48=96, 96+2059=2155. Reference section 4.7 for Busbar height.

Busbar support brace used for additional support of Busbar to rack frame, may differ dependent upon required Busbar options.

# Physical Specifications

## Rack interface Bottom.

The lower interface feature in the rack should be as defined in Figure 1,2 & 3. Datum X should be controlled from the equipment latching surface, Datum A as defined in the ORS Figure 3/7.

Figure 1: Partial Plan view on base tray rear of Busbar interface.

Figure 2: Rear view on Basetray ‘Arrow A’

Figure 3: Section thro B-B on Figure 1.

Figure 4: Image of Rack lower interface for clarity.

## Rack interface Top.

The upper interface feature in the rack should be defined as follows in Figures 5&6. This interface allows float in the depth direction so the distance from Datum A (as defined in the ORS Figure 7) can be achieved.

Figure 5: Rear face of Canopy

Figure 6: Underside view of canopy, view on ‘Arrow B’

Feature to be present in Top canopy to ensure Busbar can be fitted within tolerance as specified in ORS Figure 7 (793.4/652.6 +/-0.5 from Datum A) when being retro fitted without jig/fixture available from factory. See Figure 7.

Figure 7: Scrap view on top face of Canopy detailing Busbar locating feature.

Figure 8: Image of Rack upper interface for clarity.

Figure 9: Image of Rack Upper location feature for clarity.

## Busbar interface Bottom

The features in the Busbar cage assembly that interface with the Rack lower interface are defined as follows in Figure 10.

Figure 10: Busbar lower interface

## Busbar interface Top.

The features in the Busbar cage assembly that interface with the Rack upper interface are defined as follows in Figure 11.

Figure 11: Busbar upper interface fixing points.

## Busbar Upper location feature.

Feature to be present in upper part of Busbar, to ensure Busbar can be fitted within tolerance as specified in ORS Figure 7 (793.4/652.6 +/-0.5 from Datum A) when being retro fitted without jig/fixture available from factory. See Figure 12.

Figure 12: Side view on negative side of Busbar Assembly

## Busbar upper location jig.

The following part is only required to be supplied with Busbars, which are sold separately to the rack. This is an aid for retro fitting the Busbar assembly and ensuring OCS dimensions are met.

Figure 13: Busbar Jig plate.

Figure 14: Image showing rear top of rack, busbar fitted with jig plate.

Figure 15: Image showing jig plate from inside of rack.

## Busbar overall height

A full height Busbar will fit between the upper canopy and the lower basetray of the rack, with the distance between the upper and lower interfaces as defined in Figure 16.

Figure 16: Rear broken view of Busbar fabricated

cage detailing overall height between interfaces.

## Busbar support

For a split 2 zone Busbar, the rack support brace is positioned between zones. A fixing point is to be provided for the fixing of an additional support brace for the Busbar, this is common with the rack support brace. This position is defined in the Busbar specification number as CCCC, when specified as 1900 conforms to below:

Subsequent increase/decrease in

height to be in full OU’s, i.e. if fixing

position changes to 20OU:

958 + 48 = 1006.

If 2 fixing positions are required i.e.

CCCC=0339, dimension would be:

958-(16OU)=190

And centre to centre would be:

DD+36OU (difference between OU

Positions)

Figure 17: Rear view of Busbar showing brace fixing position

## Half height busbar

If a short lower half height Busbar is required as defined by H as in number below:

BBOCP-12-07-42H-1900-28-PS0900

Top fixing point for Busbar would be derived the same as stated in Figure 17, but subtract 13mm.

Image of Half height Busbar fixing

Centres. Note: As stated above top

Fixing position is 13mm less than full

Height centre support fixing.

i.e. For 19OU 958-13=945.0, as shown

or if brace at 20OU: 958-13+48 = 993.0

Figure 18: Rear view of Half height Busbar.

# Busbar support brace

Due to the offset fixing position between Full height and Half height Busbar assemblies and associated strength requirements, the Busbar support brace can differ to suit options. This is due to the fixing offset of 13mm as stated above in section 4.9. to suit current product in the marketplace.

Figure 19: Example of Busbar support brace for Half height (left & Right) and Full height Busbar (Centre).

# Mechanical fixing, Busbar to rack.

The busbar assembly is fixed to the rack framework with two M6 thread forming screws, in both the upper and lower position. All fixings are to be secured with a torque of 5Nm.

Fixing of the Busbar to central support brace is made with an M5 screw secured to 3Nm.

# Text boxes

A

Face of rack base.

B

Canopy to busbar  interface face.

Upper interface.

X

42OU max height, X = 2076.0mm

Subsequent increase/decrease in height to be in full OU’s

i.e. For 44OU, 2OU increase (96mm) 2076+96 = X = 2172.

Lower interface.

Half height would normally only be one zone.

Defining height of half height Busbar to coincide with brace position.

Defining Half height busbar

Half height fixing

Full height fixing