# 15kW @12V (N+1) Redundant Power Shelf Hardware V0.1

Author: Damir Klikic

# License

Contributions to this Specification are made under the terms and conditions set forth in Open Web Foundation Contributor License Agreement (“OWF CLA 1.0”) (“Contribution License”) by:

Damir Klikic -      Schneider Electric

Marlon- Galsim – Schneider Electric

Robert Bunger   - Schneider Electric

You can review the signed copies of the applicable Contributor License(s) for this Specification on the OCP website at http://www.opencompute.org/products/specsanddesign

Usage of this Specification is governed by the terms and conditions set forth in Open Web Foundation Final Specification Agreement (“OWFa 1.0”).

You can review the applicable Specification License(s) executed by the above referenced contributors to this Specification on the OCP website at http://www.opencompute.org/participate/legal-documents/

Note:  The following clarifications, which distinguish technology licensed in the Contribution License and/or Specification License from those technologies merely referenced (but not licensed), were accepted by the Incubation Committee of the OCP:

NOTWITHSTANDING THE FOREGOING LICENSES, THIS SPECIFICATION IS PROVIDED BY OCP "AS IS" AND OCP EXPRESSLY DISCLAIMS ANY WARRANTIES (EXPRESS, IMPLIED, OR OTHERWISE), INCLUDING IMPLIED WARRANTIES OF MERCHANTABILITY, NON-INFRINGEMENT, FITNESS FOR A PARTICULAR PURPOSE, OR TITLE, RELATED TO THE SPECIFICATION. NOTICE IS HEREBY GIVEN, THAT OTHER RIGHTS NOT GRANTED AS SET FORTH ABOVE, INCLUDING WITHOUT LIMITATION, RIGHTS OF THIRD PARTIES WHO DID NOT EXECUTE THE ABOVE LICENSES, MAY BE IMPLICATED BY THE IMPLEMENTATION OF OR COMPLIANCE WITH THIS SPECIFICATION. OCP IS NOT RESPONSIBLE FOR IDENTIFYING RIGHTS FOR WHICH A LICENSE MAY BE REQUIRED IN ORDER TO IMPLEMENT THIS SPECIFICATION.  THE ENTIRE RISK AS TO IMPLEMENTING OR OTHERWISE USING THE SPECIFICATION IS ASSUMED BY YOU. IN NO EVENT WILL OCP BE LIABLE TO YOU FOR ANY MONETARY DAMAGES WITH RESPECT TO ANY CLAIMS RELATED TO, OR ARISING OUT OF YOUR USE OF THIS SPECIFICATION, INCLUDING BUT NOT LIMITED TO ANY LIABILITY FOR LOST PROFITS OR ANY CONSEQUENTIAL, INCIDENTAL, INDIRECT, SPECIAL OR PUNITIVE DAMAGES OF ANY CHARACTER FROM ANY CAUSES OF ACTION OF ANY KIND WITH RESPECT TO THIS SPECIFICATION, WHETHER BASED ON BREACH OF CONTRACT, TORT (INCLUDING NEGLIGENCE), OR OTHERWISE, AND EVEN IF OCP HAS BEEN ADVISED OF THE POSSIBILITY OF SUCH DAMAGE.

# Scope

This document provides reference specifications of Gemini PSU Power Shelf

for Open Compute Rack power distribution.  It includes Electrical, Safety compliance, Environmental, Mechanical and Control Specifications. It also includes supplemental

Specification, such as power supply system redundancy, connector configuration, and signal timing.

The design specifics described herein are not intended to support all possible Open Compute system configurations.

Table of Contents

1.	License	2

1.	Scope	3

2.	Overview	4

3.	Gemini - Power Shelf Specification	5

4.	Power Shelf Configuration	5

4.1.	15kW N+1 Dual Input Power Shelf Configuration	5

4.2.	9kW N+N Dual Input Power Shelf Configuration	6

5.	Gemini - Power Shelf Specifications	7

5.1.	Shelf AC Input	7

5.2.	Input Protection	8

5.3.	Power Factor and THD	8

5.4.	Shelf Efficiency vs Load	8

With optimized shelf power management	8

5.5.	Output Specification	8

5.6.	Shelf Output Timing	9

5.7.	Power Shelf External Interface	9

5.7.1.	BBS1 Power shelf Interface	9

5.7.2.	BBS2 Power shelf Interface	9

5.7.3.	Fan and Sensor Interface	10

5.8.	Hot-Swappable Feature	10

6.	PSU Module Specification	10

6.1.	PSU Module AC Input	10

6.2.	PSU Module Input Protection	11

6.3.	PSU Module Power Factor and THD	11

6.4.	PSU Module Output	11

6.5.	PSU Module Output Timing	11

6.6.	PSU Module Efficiency vs Load	12

6.7.	PSU Module External Control Interface	12

6.8.	PSU Operating Indicators	12

6.9.	PSU Module Reliability	12

7.	ATS Specification	13

8.	RMC Specification	13

8.1.	RMC Overview	13

8.2.	RMC PSU Status Features	14

8.3.	RMC Software Interface	14

8.4.	RMC Environmental Specification	14

8.5.	RMC Relevant Standards	15

9.	Safety, Regulatory and EMC Specification	15

10.	Environmental Specifications	16

11.	Mechanical Specifications	17

11.1.	Shelf Interface Connectors	17

11.1.1.	Shelf Busbar Specs	17

11.2.	Gemini Power Shelf Drawing	18

11.2.1.	2U Power Shelf	18

11.2.1.	Shelf DC Busbar Mounting	18

11.2.1.	Shelf AC Input Connection	19

11.2.2.	Rear View 2U Power Shelf	20

11.2.3.	Power Shelf 3D Assembly Drawing	20

11.2.1.	PSU Module	21

# Overview

The Gemini PSU Power Shelf is a 2OU, 12.5VDC 15kW Open Compute Rack Power Supply.  This PSU houses (6) 3kW power modules which can be configured as 15kW N+1 or 9kW 2N for higher redundancy.  The integrated ATS allows for dual AC feed for the 15kW N+1 configuration.  Independent lithium ion battery shelves can be added for in-rack back up, with expansion up to 2 shelves for extended runtime.  The integrated RMC module allows direct interfacing with PSU modules, rack sensors, fan control, battery shelves (BBS) and host interface. It can be configured to operate in programmable constant-current mode to enable power peak shaving and support and control multiple battery shelves.   The power shelf can operate in stand-alone mode during RMC failure or temporary loss of communication.

# Gemini - Power Shelf Specification

General

| PARAMETER | DESCRIPTION |
| --- | --- |
| Input Range | 3-Phase, 5 Wire, 380/400 /415VAC |
| AC Inlet Configuration | Single input or dual input with Integrated Automatic Transfer Switch |
| Redundant Configuration | Single input path 3-Phase feed: 15kW N+1, 12kW N+2 or 9kW N+3 Dual input path: 15kW N+1 (with ATS) or 9kW 3+3 double redundancy w/o ATS |
| Integrated RMC Module | Direct Interface to PSU Modules, Fan Controller, Rack Sensor and Host Interface |
| Rated Power | 15kW (5+1 configuration with ATS) |
|  | 9kW (3+3 Configuration without ATS) |
| Efficiency | Meet 80 Plus Platinum Energy Efficiency Standard |
| Output Connection | 1 set of output blades for 12V DC output |
| +12VSB Standby Output | 60W (Standby output 12.5V/5A) |
| BBS Interface | Dual BBS Interface for Backup and Grid Peak Shaving |
| RMC Power module Interface | 3-Channels I2C PMBus (CH1: PSU Modules, CH2: BBS1 Shelf, CH3: BBS2 Shelf) |
| Dimensions (W×H×D) | 534.3×93×650mm (overall: 534.3×93×889.5) |

Connectors

| description | type | manufacture | mpn |
| --- | --- | --- | --- |
| Input Connector | 3-phase input (2pcs) | Molex | 042820-5223 |
| BBS External Interface | 16pin / 1pcs | Molex | 501876-1640 |
| BBS Interface for Extended Runtime | RJ45 / 1pcs | Molex | 043202-8113 |
| FAN and Sensor Backplane Interface | 30pin / 2pcs | Molex | 501876-3040 |
| +12VSB / BGND | 4Pin / 1pcs | Molex | 172316-1104 |

# Power Shelf Configuration

## 15kW N+1 Dual Input Power Shelf Configuration

This Power Shelf configuration provides dual input and 5+1 PSU redundancy through the integrated Automatic Transfer Switch (ATS) and it’s shown in Fig1. The ATS module is removable for easy assembly and maintenance.

The 380/400/415Vac 3ɸ input is connected to the Molex backplane connector with a rating of 600Vac/50A per terminal.

The Power Shelf also integrates hot-swappable RMC module, the RMC module provides interface with the PSU modules, battery shelves, rack sensors, rack fan controller(s) and host interface.

#### Figure 1: Gemini 15kW 5+1 Power Shelf Block Diagram

## 9kW N+N Dual Input Power Shelf Configuration

Power shelf can be also configurated for dual input with 3+3 PSU redundancy.

For 380/400/415Vac 3ɸ inputs the Molex backplane connector (42820-5223) are provided with a rating of 600Vac/50A per terminal.  The connection block diagram is presented in Fig.2.

#### Figure 2: Gemini 9kW 3+3 Power Shelf Block Diagram

# Gemini - Power Shelf Specifications

## Shelf AC Input

| PARAMETEr | DESCRIPTION/Condition | Min | nom | max | unit |
| --- | --- | --- | --- | --- | --- |
| Input connector J64 & J65 |  |  |  |  |  |
| AC Input Configuration AC Nominal Input Voltage | 3ɸ 5-Wire Line to Line input |  | 400 |  | VAC |
| AC Input Voltage Range |  | 312 |  | 456 | VAC |
| Max Input Current | Per line |  |  | 17 | Arms |
| Input Frequency |  | 47 | 50/60 | 63 | Hz |

## Input Protection

| PARAMETEr | DESCRIPTION/Condition | Min | nom | max | unit |
| --- | --- | --- | --- | --- | --- |
| Under-Voltage Protection | Line to Line input | 300 |  |  | VAC |
| Inrush Current Limiting |  |  |  | 150 | % |
| Overload Shutdown Protection |  |  |  | ≥ 110 | % |
| Other Protections | OVP, OTP, Short Circuit |  |  |  |  |

## Power Factor and THD

| PARAMETEr | DESCRIPTION/Condition | Min | nom | max | unit |
| --- | --- | --- | --- | --- | --- |
| Power Factor | ≥ 20% Load | >0.96 | 0.97 |  |  |
|  | ≥ 50% to 100% Load | >0.98 | 0.99 |  |  |
| THD | ≥ 30% Load |  |  | < 8 | % |
|  | ≥ 50% Load |  |  | < 6 | % |
|  | ≥ 80% Load |  |  | < 5 | % |
|  | 100% Load |  |  | < 5 | % |

## Shelf Efficiency vs Load

| PARAMETEr | DESCRIPTION/Condition | Min | nom | max | unit |
| --- | --- | --- | --- | --- | --- |
| Efficiency | 20% Load |  |  | >90 | % |
|  | 50% Load |  |  | 94 | % |
|  | 80% Load |  |  | 94 | % |
|  | 100% Load |  |  | >91 | % |

## With optimized shelf power management

| PARAMETEr | DESCRIPTION/Condition | Min | nom | max | unit |
| --- | --- | --- | --- | --- | --- |
| Efficiency | 20% Load |  |  | 94 | % |
|  | 50% Load |  |  | 94 | % |
|  | 80% Load |  |  | 93.5 | % |
|  | 100% Load |  |  | 93 | % |

## Output Specification

| PARAMETEr | DESCRIPTION/Condition | Min | nom | max | unit |
| --- | --- | --- | --- | --- | --- |
| Main Output Busbar |  |  |  |  |  |
| Nominal Output Voltage |  |  | 12.5 |  | VDC |
| Output Voltage Regulation |  | -2 |  | 2 | % |
| Nominal Output Power 1 | 3+3 configuration, Ta<45°C |  | 9000 |  | W |
| Nominal Output Power 2 | 5+1 configuration, Ta<45°C |  | 15000 |  | W |
| Nominal Output Current 1 | 3+3 configuration, Ta<45°C |  | 720 |  | ADC |
| Nominal Output Current 2 | 5+1 configuration, Ta<45°C |  | 1200 |  | ADC |
| Output Ripple voltage |  |  |  | 120 | mV |
| Dynamic Load Regulation |  |  | +-3% |  | % |
| PSU Module Current Sharing Tolerance | > 40% Load |  | 5 |  | % |
| Response Time |  |  |  | <500 | uS |
| Output Voltage Temperature Coefficient |  |  |  | 0.02 | %/°C |
| Shelf Busbar Voltage Drop | 1200A Load @ 60°C |  |  | 17 | mV |
| Overload Capability | LED warning signal, Output voltage Regulated. |  |  | 110 | % |

## Shelf Output Timing

| PARAMETEr | DESCRIPTION/Condition | Min | nom | max | unit |
| --- | --- | --- | --- | --- | --- |
| Start-Up Time | PS_ON to Output Voltage Regulation |  |  | 50 | mS |
| Hold-Up Time | 100% Load | 12 |  |  | mS |
| Output Voltage Overshoot | Turn-On and Turn-Off |  |  | <10 | % |
| Dynamic Response time | 10% -90% Load Transient |  |  | <500 | uS |

## Power Shelf External Interface

### BBS1 Power shelf Interface

| BBS1 Interface | DESCRIPTION/Condition |
| --- | --- |
| BBS_On | RMC Signal to BBS Shelf for ON/OFF control |
| BBS_PWOK | BBS Signal to RMC to indicate Main 12V output is within regulated range during Battery backup mode. |
| BBS_Present | BBS Shelf signal to RMC to indicate the BBS is connected to RMC interface port. |
| BBS_AC_Good | RMC Signal to BBS Shelf to indicate that the AC input voltage is within range to enable BBS Charging mode and utility peak shaving function. |
| BBS_Alert | BBS Shelf Signal to RMC to indicate Fault conditions such as OVP, OCP, OTP. |
| PMBus CLK2 | RMC PMBus I2C Channel2 Clock signal for PMBus protocol data transfer. |
| PMBus SDA2 | RMC PMBus I2C Channel2 Data signal for PMBus protocol data transfer |

### BBS2 Power shelf Interface

| BBS2 Interface | DESCRIPTION/Condition |
| --- | --- |
| BBS_On | RMC Signal to BBS Shelf for ON/OFF control |
| BBS_PWOK | BBS Signal to RMC to indicate Main 12V output is within regulated range during Battery backup mode. |
| BBS_Present | BBS Shelf signal to RMC to indicate the BBS is connected to RMC interface port. |
| BBS_AC_Good | RMC Signal to BBS Shelf to indicate that the AC input voltage is within range to enable BBS Charging mode and utility peak shaving function. |
| BBS_Alert | BBS Shelf Signal to RMC to indicate Fault conditions such as OVP, OCP, OTP. |
| PMBus CLK3 | RMC PMBus I2C Channel3 Clock signal for PMBus protocol data transfer. |
| PMBus SDA3 | RMC PMBus I2C Channel3 Data signal for PMBus protocol data transfer |

### Fan and Sensor Interface

| Rack Fan and sensor Interface | DESCRIPTION/Condition |
| --- | --- |
| PWM | 10-Channels Interface for Fan Speed Control |
| TACH | 10-Channels Interface for Fan Speed and Fault Monitoring |
| I2C | 10-Channels for I2C compatible sensor interface |
| Digital I/O | Control input/output for fan and sensor alarm and control signal |
| +12VSB | Power supply voltage for sensor signal conditioning circuit. |

## Hot-Swappable Feature

- PSU Hot-Swap 0-100% Load Condition

- PSU Hot-Swap during RMC Online Communication

- RMC Hot-Swap during PSU Operation

- Replaceable ATS module.

# PSU Module Specification

## PSU Module AC Input

| PARAMETEr | DESCRIPTION/Condition | Min | nom | max | unit |
| --- | --- | --- | --- | --- | --- |
| AC Input Configuration AC Nominal Input Voltage | 1PH 3-Wire (L-N-G) Line to Neutral input |  | 240 |  | VAC |
| AC Input Voltage Range |  | 180 |  | 264 | VAC |
| Max Input Current |  |  |  | 17 | Arms |
| Input Frequency |  | 47 | 50/60 | 63 | Hz |

## PSU Module Input Protection

| PARAMETEr | DESCRIPTION/Condition | Min | nom | max | unit |
| --- | --- | --- | --- | --- | --- |
| Under-Voltage Protection | Line to Line input |  | 175 |  | VAC |
| Inrush Current Limiting |  |  |  | <150 | % |
| Overload Protection |  |  |  | ≥ 110 | % |
| Other Protections | OVP, Short Circuit, OTP |  |  |  |  |

## PSU Module Power Factor and THD

| PARAMETEr | DESCRIPTION/Condition | Min | nom | max | unit |
| --- | --- | --- | --- | --- | --- |
| Power Factor | ≥ 20% Load | >0.96 | 0.97 |  |  |
|  | ≥ 50% to 100% Load | >0.98 | 0.99 |  |  |
| THD | ≥ 30% Load |  |  | <8 | % |
|  | ≥ 50% Load |  |  | <6 | % |
|  | ≥ 80% Load |  |  | <5 | % |
|  | 100% Load |  |  | <5 | % |

## PSU Module Output

| PARAMETEr | DESCRIPTION/Condition | Min | nom | max | unit |
| --- | --- | --- | --- | --- | --- |
| Nominal Output Voltage |  |  | 12.5 |  | VDC |
| Output Voltage Regulation |  | -1 |  | +1 | % |
| Nominal Output Power | Ta<45°C |  | 3000 |  | W |
| Output Ripple voltage |  |  |  | 120 | mV |
| Dynamic Load Regulation |  | -3 |  | +3 | % |
| Load Sharing Unbalanced | 50% Load |  | 5 |  | % |
| Response Time |  |  |  | <500 | uS |
| Output Voltage Temperature Coefficient |  |  |  | 0.02 | %/°C |

## PSU Module Output Timing

| PARAMETEr | DESCRIPTION/Condition | Min | nom | max | unit |
| --- | --- | --- | --- | --- | --- |
| Start-Up Time | PS_ON to Output Voltage Regulation |  |  | 50 | mS |
| Hold-Up Time | 100% Load | 12 |  |  | mS |
| Output Voltage Overshoot | Turn-On and Turn-Off |  |  | <10 | % |
| Dynamic Response time | 10% -90% Load Transient |  |  | <500 | uS |

## PSU Module Efficiency vs Load

| PARAMETEr | DESCRIPTION/Condition | Min | nom | max | unit |
| --- | --- | --- | --- | --- | --- |
| Efficiency | ≥ 20% Load |  | 93 |  | % |
|  | ≥ 40% Load |  | 94.3 |  | % |
|  | ≥ 60% Load |  | 93.5 |  | % |
|  | ≥ 80% Load |  | 92.6 |  | % |
|  | 100% Load |  | 91.5 |  | % |

## PSU Module External Control Interface

| PARAMETEr | DESCRIPTION/Condition |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| PS_On | Power On/Off Signal from RMC |  |  |  |  |
| PWOK | PSU Signal to RMC to indicate +12V output is within Regulating range |  |  |  |  |
| Alert | PSU Signal to RMC to indicate Fault condition |  |  |  |  |
| Present | PSU signal to RMC to indicate PSU is connected to the Powershelf |  |  |  |  |
| Vin_Ok | PSU Signal to RMC to indicate AC Input voltage is within range. |  |  |  |  |
| A2, A1, A0 | PSU PMBus address for RMC communication |  |  |  |  |
| CLK, SDA | I2C/PMBus Interface to RMC Module |  |  |  |  |

## PSU Operating Indicators

| PARAMETEr | DESCRIPTION/Condition |
| --- | --- |
| AC OK | Green: LED ON, AC Input is within range |
| DC_OK | Yellow: LED ON, DC Output voltage is within range |
| FAULT | Red: LED ON, Fault condition (OVP, OCP, OTP, UVP, Fan Failure) |

## PSU Module Reliability

| PARAMETEr | DESCRIPTION/Condition | Min | nom | max | unit |
| --- | --- | --- | --- | --- | --- |
| MTBF | 45C/100% Load | 250,000 |  |  | Hrs |
| Diode/Mosfet De-rating | 100% Load |  |  | 85 | % |
| Bulk Cap Voltage De-rating | Maximum Input Voltage |  |  | 90 | % |
| Temperature De-Rating | 100% Load |  |  | 85 | % |
| HALT Low Temperature |  |  |  | -30 | °C |
| HALT High Temperature |  |  |  | 70 | °C |
| HALT Vibration |  |  |  | 35 | G |

# ATS Specification

| PARAMETEr | DESCRIPTION/Condition | Min | nom | max | unit |
| --- | --- | --- | --- | --- | --- |
| AC Input Configuration AC Nominal Input Voltage | 3ɸ 5-Wire Line to Line input |  | 400 |  | VAC |
| AC Input Voltage Range |  | 300 |  | 456 | VAC |
| Max Input Current | Per line |  |  | 17 | Arms |
| Input Frequency |  | 47 | 50/60 | 63 | Hz |
| ATS Transfer Time |  |  | 8 | <10 | ms |

# RMC Specification

## RMC Overview

Rack Management Controller (RMC) module is designed to integrate directly into OCP Power Shelf, providing interfaces for monitoring and control of PSU modules, associated battery shelves, rack sensors and controls and datacenter management applications.

The RMC module communicates to the induvial PSU modules via PMBus/I2C Channel 1 using PMBus 1.2 protocol and RMC simple signaling for PSU controls.

The RMC communicates to the BBS1 shelf via PMBus/I2C Channel 2 and BBS2 Shelf via PMBus/I2C Channel 3 using PMBus 1.2 protocol and RMC simple signaling for BBS controls.

RMC Interface to PSU Module:

- PSON: RMC Signal to PSU module for PSU ON/OFF control

- PWOK: PSU Signal to RMC to indicate Main 12.5V output is within regulated range.

- PSU_Present: PSU module signal to RMC to indicate the PSU module is inserted in the PSU Shelf slot.

- PSU_VinOK: PSU Signal to RMC to indicate that the AC input voltage is within range.

- PSU_Alert: PSU Signal to RMC to indicate Fault conditions such as OVP, OCP, OTP.

- PMBus CLK1: RMC clock signal for PMBus protocol data transfer

- PMBus SDA1: RMC/PSU data signal for PMBus/I2C data transfer.

RMC Interface to BBS Shelf:

- BBS_ON: RMC Signal to BBS Shelf for ON/OFF control

- BBS_PWOK: BBS Signal to RMC to indicate Main 12V output is within regulated range during Battery backup mode.

- BBS_Present: BBS Shelf signal to RMC to indicate the BBS is connected to RMC interface port.

- BBS_AC_Good: RMC Signal to BBS Shelf to indicate that the AC input voltage is within range to enable BBS Charging mode and utility peak shaving function.

- PSU_Alert: BBS Shelf Signal to RMC to indicate Fault conditions such as OVP, OCP, OTP.

- PMBus CLK2: RMC clock signal for PMBus protocol data transfer to BBS1 Shelf.

- PMBus SDA2: RMC/BBS1 data signal for PMBus/I2C data transfer to BBS1 Shelf.

- PMBus CLK3: RMC clock signal for PMBus protocol data transfer to BBS2 Shelf.

- PMBus SDA3: RMC/BBS2 data signal for PMBus/I2C data transfer to BBS2 Shelf.

## RMC PSU Status Features

- Input and output voltage

- Input and output current

- Fan speed

- PSU protection log information

- Ambient temperature

- FRU information (such as Manufacturer and Product Name, Part/Model/SN & Revision

## RMC Software Interface

| PARAMETEr | DESCRIPTION/Condition |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Linux | AMI Linux distribution for the iBMC |  |  |  |  |
| IPMI | AMI MegaRAC IPMI 2.0 |  |  |  |  |
| DCMI | DCMI 1.5 subset |  |  |  |  |
| CLI | DMTF SM-CLP (AMI implementation) |  |  |  |  |
| CLI Command set baseline | CLI specification, v1.0 2012/5/6 |  |  |  |  |
| PMBus | PMBus specification Part II - Command Language, Rev 1.2, 2019-09 |  |  |  |  |

## RMC Environmental Specification

| PARAMETEr | DESCRIPTION/Condition | Min | nom | max | unit |
| --- | --- | --- | --- | --- | --- |
| Operating Ambient Temperature |  | 0 |  | 50 | °C |
| Storage Temperature |  | -40 |  | 85 | °C |
| Operating Relative Humidity | Non-Condensing | 10 |  | 90 | % |
| Storage Relative Humidity | Non-Condensing | 10 |  | 95 | % |
| Operating altitude | No De-rating |  |  | 2000 | m |
| Operating vibration | 0.5 g acceleration ion, 1.5 mm amplitude, 5 to 500 Hz, 10 sweeps at 1 octave/minute for each of the three axes |  |  |  |  |
| Non-operating vibration | 1.0 g acceleration, 3/0mm amplitude, 5 to 500 Hz, 10 sweeps at 1 octave/minute for each of the three axes. |  |  |  |  |

## RMC Relevant Standards

| PARAMETEr | DESCRIPTION/Condition | Min | nom | max | unit |
| --- | --- | --- | --- | --- | --- |
| Open Computing | Open Compute Open Rack Standard V1.1 Open Compute Project Open Hardware Management Proposed Specification for Remote Machine Management Version 1.01 2/25/2014 |  |  |  |  |
| PMBus | Part I – General Requirements, Transport and Electrical Interface, Rev 1.2., 2010-09-06 Part II – Command Language, Rev 1.2., 2010-09-06 |  |  |  |  |
| IPMI | Intelligent Platform Management Interface (IPMI 2.0) |  |  |  |  |
| DMTF/CLP | DMTF Server Management Command Line (SM CLP) Specification (DSP0214, v1.0.2) |  |  |  |  |
| SNMP/PET | Platform Event Trap Specification, v1.0, revision 1.00 |  |  |  |  |
| DCMI | Data Center Management Interface specification version 1.5 |  |  |  |  |

# Safety, Regulatory and EMC Specification

| Parameter | description / condition | criterion |
| --- | --- | --- |
| Agency Approvals | Approved to the latest revisions/amendments of the following standards: (pending) UL 60950-1 Second Edition CAN/CSA-C22.2 No. 60950-1-07 Second Edition IEC 60950-1:2005 EN 60950-1:2006 | Approved by independent body (see CE Declaration) (pending) |
| Insulation | Input (L/N) to case (PE) Input (L/N) to output Output to case (PE) | Basic Reinforced Functional |
| Creepage / Clearance | Primary (L/N) to protective earth (PE) Primary to secondary |  |
| Electrical Strength Test | Input to case Input to output (tested by manufacturer only) | Min. 2121Vdc Min. 4242Vdc |
| Max. Leakage Current | AC input voltage of TBD VAC, line frequency of 50Hz and a temperature of 25°C. | TBD A |
| Conducted Emission | EN55022 / CISPR 22: 0.15 … 30 MHz, QP and AVG | Class A |
| Radiated Emission | EN55022 / CISPR 22: 30 MHz … 1 GHz, QP | Class A |
| Harmonic Emissions (per module) | IEC61000-3-2, Vin = 115/230 VAC, 50 Hz, 100% Load | Class A |
| Acoustical Noise | Sound power statistical declaration (ISO 9296, ISO 7779, IS9295) @50% load | 60 dBA |
| AC Flicker | IEC / EN 61000-3-3, dmax < 3.3% |  |
| ESD Contact Discharge | IEC / EN 61000-4-2, ±8 kV, 25+25 discharges per test point (metallic case, LEDs, connector body) | A |
| ESD Air Discharge | IEC / EN 61000-4-2, ±15 kV, 25+25 discharge per test point (user accessible surfaces) | A |
| Radiated Electromagnetic Field | IEC / EN 61000-4-3, 10 V/m, 1 kHz/80% Amplitude Modulation, 1 μs Pulse Modulation, 10 kHz…2 GHz | A |
| Burst | IEC / EN 61000-4-4, level 3 AC port ±2 kV, 1 minute DC port ±1 kV, 1 minute | A |
| Surge | IEC / EN 61000-4-5 Line to earth: level 3, ±2 kV Line to line: level 2, ±1 kV | A |
| RF Conducted Immunity | IEC/EN 61000-4-6, Level 3, 10 Vrms, CW, 0.1 … 80 MHz | A |

# Environmental Specifications

| PARAMETEr | DESCRIPTION/Condition | Min | nom | max | unit |
| --- | --- | --- | --- | --- | --- |
| Operating Temperature | @ full load, up to 4000 m: @ full load, up to 1800 m: @ 75% load, up to 1800 m: | -5 -5 -5 |  | +35 +45 +55 | °C |
| Non-Operating Temperature |  | -40 |  | +70 | °C |
| Humidity | Operating: @ at 40 °C, non-condensing Non-Operating: non-condensing | 7 5 |  | 93 95 | %RH |
| Altitude | Operation: Non-Operation: |  |  | 4000 13000 | m |
| Shock | Operating: 11ms half-sine shocks in Z axis 10+ve, 10-ve Non-Operating: 11ms half-sine shocks in Z axis 10+ve, 10-ve |  | 5 30 |  | g |
| Vibration | Operating: 0.2g rms random Non-Operation: 1g rms random | 5 |  | 500 | Hz |
| Acoustic Noise Emissions | @ normal operation, and 50% load sharing fan speed |  |  | 70 7000 | dBA rpm |
| Cooling | When equipped with operating PSUs |  |  | 50 | Pa |

# Mechanical Specifications

| PARAMETEr |  |
| --- | --- |
| Rack Unit | 2OU |
| Dimensions (W×H×D) | 534.3×93×650mm (overall: 534.3×93×889.5) |

## Shelf Interface Connectors

| description | type | manufacture | mpn |
| --- | --- | --- | --- |
| Input Connector | 3-phase input (2pcs) | Molex | 042820-5223 |
| BBS External Interface | 16pin / 1pcs | Molex | 501876-1640 |
| BBS Interface for Extended Runtime | RJ45 / 1pcs | Molex | 043202-8113 |
| FAN and Sensor Backplane Interface | 30pin / 2pcs | Molex | 501876-3040 |
| +12VSB / BGND | 4Pin / 1pcs | Molex | 172316-1104 |

### Shelf Busbar Specs

| PARAMETEr | DESCRIPTION/Condition | Min | nom | max | unit |
| --- | --- | --- | --- | --- | --- |
| Voltage at point of connection to bus bar | Shelf output voltage at no load. |  | 12.5 |  | Vdc |
| Busbar current Density |  |  |  | 3.5 | A/mm² |
| Bus bar material | copper with nickel plating. |  | CC100 |  |  |
| Bus bar maximum Current |  |  |  | 1200 | Adc |
| Bus bar maximum voltage drop | Voltage drop with respect to the location of the PSU module to the shelf bus bar |  |  | 40 | mV |
| Bus bar maximum power dissipation | Power loss with respect to the location of the PSU module to the shelf bus bar |  |  | 40 | Watts |
| Shelf Internal Bus bar Temperature | 40C Ambient Temperature |  |  | 70 | °C |

## Gemini Power Shelf Drawing

### 2U Power Shelf

### Shelf DC Busbar Mounting

### Shelf AC Input Connection

### Rear View 2U Power Shelf

3ɸAC Input B

3ɸAC Input A

12V Busbar

BBS2 Port

BBS1 Port

12VSB

Fan/Sensor Port/IO

Fan/Sensor Port/IO

### Power Shelf 3D Assembly Drawing

ATS

PSU

RMC

2U Shelf

### PSU Module