## Slide 1: Thermal Model Description
Rev 01
4/27/2017
Yueming Li, Thermal Engineer, Facebook
John Fernandes, Thermal Engineer, Facebook
Jia Ning, Hardware Engineer, Facebook

## Slide 2: Fixed Parameters for CFD
Use Enumeration #7 as starting point
DRAM
  8*DRAMs @ 0.4W each
I/O module
  2*QSFP optical module @ 3.5W each
ASIC size
  With DRAM: 33*33mm
  Without DRAM: 25*25mm
Airflow approach to card
  Cold aisle: 35°C (towards I/O module)
  Hot aisle: 55°C (towards DRAM/ASIC)
PCB top clearance
  Follow Mezz 2.0 spec (2.9mm)
QSFP @ 3.5W each
ASIC @ 20 ~ 30W
Connector A
Connector B
DRAM @ 0.4W each

## Slide 3: Variables for CFD
ASIC Power
  Range from 15W to 35W
Mechanical
  Baseboard size
    4 Sizes in total: 7a, 7b, 7c, 7d
    As start, choose two form factors: 7a and 7d
  Connector height
    Choose 8mm for 7a
    Choose 12mm for 7d
  Cutout size
    I/O ports only for 7a
    I/O ports + heat sink for 7d
  Airflow direction
    Cold aisle, hot aisle
  LFM
    150 ~ 300 LFM for cold aisle
    150 ~ 500 LFM for hot aisle
7a: Smallest Form Factor
7d: Increase Both Width and Depth
Original Mezz 2.0
7b: Increase Width
7c: Increase Depth

## Slide 4
Cut-out Sizes
I/O ports only
  The cutout for I/O will fit into all optical modules listed in Mezz 2.0 spec, including QSFP, RJ45 and SFP
  Cutout width and depth are 65.79mm * 54.8mm
I/O ports + heat sink
  Besides I/O cutout, additional heat sink cutout enables higher fins for ASIC
  Cutout width and depth are 65.79mm* 110.05mm
    110.05mm is the total depth of 7a mezzanine PCB
IO ports only cutout for 7a
IO ports + heat sink cutout for 7d

## Slide 5: Cases for CFD - Input
Please note
  The objective is to study both ends of the spectrum as a starting point
    Thermally least favorable configuration – 7a + “IO ports only” cut-out + 8mm connector
    Thermally most favorable configuration – 7d + “IO ports + heat sink” cut-out + 12mm connector
  Results might not give a solution, but should provide a clear direction for further thermal analysis
Case # |  | Input parameters |  |  |  |  |  |  | 
 | I/O | ASIC 1 Power (W) | ASIC 1 Location | Connector Height (mm) | PCB Board Size | DRAM Location | Cut-out | Heat Sink + BGA Max Height | Airflow Direction or I/O Location
A1 | 2x QSFP-Bottom | 15 | Bottom | 8 | 7a | N/A | IO Ports Only | 7 | Cold-aisle
A2 | 2x QSFP-Bottom | 20 | Bottom | 8 | 7a | N/A | IO Ports Only | 7 | Cold-aisle
A3 | 2x QSFP-Bottom | 25 | Bottom | 8 | 7a | N/A | IO Ports Only | 7 | Cold-aisle
A4 | 2x QSFP-Bottom | 30 | Bottom | 8 | 7a | N/A | IO Ports Only | 7 | Cold-aisle
A5 | 2x QSFP-Bottom | 15 | Bottom | 8 | 7a | N/A | IO Ports Only | 7 | Hot-aisle
D1 | 2x QSFP-Bottom | 35 | Bottom | 12 | 7d | Bottom | IO Ports + Heat Sink | 16 | Cold-aisle
D2 | 2x QSFP-Bottom | 30 | Bottom | 12 | 7d | Bottom | IO Ports + Heat Sink | 16 | Cold-aisle
D3 | 2x QSFP-Bottom | 25 | Bottom | 12 | 7d | Bottom | IO Ports + Heat Sink | 16 | Cold-aisle
D4 | 2x QSFP-Bottom | 20 | Bottom | 12 | 7d | Bottom | IO Ports + Heat Sink | 16 | Cold-aisle
D5 | 2x QSFP-Bottom | 20 | Bottom | 12 | 7d | Bottom | IO Ports + Heat Sink | 16 | Hot-aisle

## Slide 6: Cases for CFD - Output
Output parameters |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 
ASIC Tcase_max (°C) |  |  |  |  |  | DRAM Tcase_max (°C) |  |  |  |  |  | I/O Module Tcase_max (°C) |  |  |  |  |  | 
105°C |  |  |  |  |  | 95°C |  |  |  |  |  | 85°C |  |  |  |  |  | 
150 | 200 | 250 | 300 | 400 | 500 | 150 | 200 | 250 | 300 | 400 | 500 | 150 | 200 | 250 | 300 | 400 | 500 | LFM
Component | Tcase_max (°C)
DRAM | 95
QSFP | 85
ASIC | 105
Table 1. Specs for components

## Slide 7
FloTherm Model
Please note the following initial definitions in the models
  PCB layer definition for thermal conductivity
  2-resistor models for ASIC and DRAM
  Simplified block with embedded source for QSFP modules
Any feedback per the above would be greatly appreciated
170426 Mezz 3.0 Case D1.pdml
170426 Mezz 3.0 Case A1.pdml