## Slide 2: KEYNOTE: INDICATOR SPECIFICATION PROPOSAL
Michael Haken, Mechanical Engineer, Facebook.

## Slide 3
Objective
Adopt an OCP specification where indicators are clearly visible, consistent, accommodate color-blind data center personnel, only communicate actionable information, and do not conflict with other diagnostic tools.

## Slide 4
Guiding Principals
Indicators Should:
Be Consistent – common symbols, LED colors, intensity, message
Have a Purpose – must provide actionable information
Be Simple – no decoder ring necessary
Never Conflict with Indicators on other Products

## Slide 5
Indicator Colors

## Slide 6
Indicator Intensity

## Slide 7
Indicator Intensity – View Angle
+/-40 degree view angle horizontally and vertically
+/- 25% Luminosity intensity within this range
+/- 55 degree view angle whenever possible
Indicator cross-talk should not cause an increase of more than 20 Cd/m^2 in adjacent indicators

## Slide 8
Indicator Behaviors

## Slide 9
Indicator Placement
Indicators should be visible on the front or rear panel of a system when viewing the panel from a perpendicular direction.
Indicators should always be surrounded by a panel to reduce background visual noise and provide a location for printed legends.
Indicator pairs must be arranged as: blue-left/amber-right, or blue-above/amber-below

## Slide 10
Indicator Nomenclature

## Slide 11
Indicator States

## Slide 12: Indicator States As Applied to Specific Hardware